25-12.045 Inactive Gas Service Lines.

(1) The following actions shall be taken for inactive gas service lines that have been used, but have become inactive without reuse:

(a) If there is no prospect for reuse, the service line shall be retired and physically abandoned within three months.

(b) After a service line has been inactive for a period of two years, if there is a prospect for reuse of the line, one of the following actions shall be taken within six months:

1. Disconnect the service line from all sources of gas and abandon or remove;

2. A valve on the service line shall be locked in the closed position and the service line plugged to prevent the flow of gas;

3. Remove the meter and plug the end of the service line to prevent the flow of gas.

(c) After five years of inactivity, service lines shall be retired and physically abandoned within six months.

(2) To physically abandon a service line, the operator must disconnect the service line from all sources of gas at the nearest point to the gas main. Where the appropriate governmental authority prohibits cutting pavement, the service line shall be disconnected at the nearest point not under a paved surface. The stub of the service line, the short section of the remaining service line to the main, shall be disconnected closer to the main or at the main, if at some later date it becomes accessible during normal operations.

(3) Records must be kept of the size, material, and location of all remaining service line stubs. These records must be readily available to personnel assigned to pipeline locating activities.

Specific Authority 368.05(2) FS. Law Implemented 368.05(2) FS. History–New 9-21-74, Repromulgated 10-7-75, Amended 10-2-84, Formerly 25-12.45, Amended 1-7-92.