## 40A-3.504 Location.

(1) Wells shall be located so as not to pose a threat of contamination to the District’s water resources and to provide for the protection of the health, safety, and welfare of the user.

(2) Minimum spacing between wells and sanitary hazards such as septic tanks, drainfields, ground water contamination areas, cesspools, etc. shall be as specified by Section 381.0065 and Chapter 373, Part III, F.S., and the respective rules of the Department of Health and Rehabilitative Services and the Florida Department of Environmental Protection.

(3) The following minimum distances shall apply, unless an exemption has been obtained. The following list is not inclusive or exhaustive, and further reference to Chapters 62-524, 62-550, 62-555, 62-610, 64E-6 and 64E-8, F.A.C., should be made.

(a) Landscape and recreational area irrigation wells shall be located a minimum of seventy-five (75) feet from a sanitary hazard.

(b) Landscape and recreational area irrigation wells shall be located outside ground water contamination areas delineated by the Department of Environmental Protection in Rule 62-524.430, F.A.C.

(c) Domestic Self Supply water wells shall be located a minimum distance of twenty-five (25) feet from building foundations treated with pesticides.

(d) Domestic Self Supply water wells shall be located a minimum distance of seventy-five (75) feet from a sanitary hazard, such as an onsite sewage disposal system (OSDS).

(e) Domestic Self Supply water wells shall be located a minimum distance of one hundred and seventy-five (175) feet from storage and treatment facilities of livestock farms.

(f) Domestic Self Supply water wells within ground water contamination areas delineated by the Department of Environmental Protection shall be located as specified in Rule 62-524.500, F.A.C. The delineated areas are found in Rule 62-524.430, F.A.C.

(g) Limited Use Public Supply wells, constructed under the provisions of Chapter 64E-8, F.A.C., shall be located a minimum distance of one hundred (100) feet from a sanitary hazard, such as an onsite sewage disposal system (OSDS), if the sewage flow is less than 2000 gallons per day or 200 feet from an OSDS with sewage flows of 2000 gallons per day or more.

(h) Limited Use Public Supply wells, constructed under the provisions of Chapter 64E-8, F.A.C., within ground water contamination areas delineated by the Department of Environmental Protection shall be located as specified in Rule 62-524.500, F.A.C. The delineated areas are found in Rule 62-524.430, F.A.C.

(i) Public water supply wells constructed under provisions of Chapter 62-555, F.A.C., DEP Public Supply Wells, must be located a minimum distance of two hundred (200) feet from a sanitary hazard, such as an onsite sewage disposal system (OSDS).

(j) Public water supply wells shall be located a minimum distance of one hundred (100) feet from other sanitary hazards as identified in Department of Environmental Protection Rule 62-550.200, F.A.C.

(k) Public water supply wells shall be located a minimum distance of three hundred (300) feet from storage and treatment facilities of livestock farms.

(l) Public water supply wells shall be located a minimum distance of five hundred (500) feet from areas used for land application of reclaimed water.

(m) Public water supply wells within ground water contamination areas delineated by the Department of Environmental Protection shall be located as specified in Rule 62-524.500, F.A.C. The delineated areas are found in Rule 62-524.430, F.A.C.

(4) The District shall increase these distances if necessary to protect the health, safety, and welfare of individuals who may be exposed to ground water contamination through ingestion, inhalation, or dermal absorption.

(5) Exemptions to the above specified distances may be obtained from the District as provided by Rule 40A-3.051, F.A.C. The exemption request will be evaluated on such criteria as gradient, well location, natural barriers, impermeable geological strata, water quality sampling, grouting, and the use of water treatment systems acceptable to the Department of Environmental Protection or the local health unit.

(6) In subdivisions platted after January 1, 1972, domestic self-supplied potable wells may be located on lots with onsite sewage disposal systems (OSDS), provided that each lot has a minimum area of at least one-half acre and either a minimum dimension of one hundred (100) feet or mean of at least one hundred (100) feet of the side bordering the street and the distance formed by a line parallel to the side bordering the street drawn between the two most distant points of the remainder of the lot, and providing the projected daily domestic sewage flow does not exceed an average of 1,500 gallons per acre per day.

Rulemaking Authority 373.026, 373.044, 373.103, 373.113, 373.171, 373.308, 373.309, 373.326, 373.337 FS. Law Implemented 373.306, 373.308, 373.309, 373.326 FS. History–New 1-9-86, Amended 4-5-88, 8-1-89, 12-1-90, 2-19-91, 11-1-92, 11-1-93, 11-1-95.