- 59A-3.081 Physical Plant Requirements for Mobile Surgical Facilities.

The following are special requirements for Mobile Surgical Facilities.

(1) A mobile surgical facility is a mobile facility as defined in Section 395.002, F.S., and that provides elective surgical care under contract with the Department of Corrections or a private correctional facility operating pursuant to Chapter 957, F.S.

(2) General Requirements: In addition to the codes and standards referenced in this rule, the mobile surgical facility shall be in compliance with the requirements of the National Fire Protection Association (NFPA) Life Safety Code 101, New Ambulatory Health Care Occupancy, adopted by the State Fire Marshal and described in Rule Chapter 69A-60, F.A.C.

(a) Site Requirements:

1. A level concrete pad designed for the structural loads of the facility in accordance with the Florida Building Code, adopted by the Florida Building Commission and described in Rule 61G20-41.001, F.A.C.

2. Walls, fences or concrete-filled steel bollards around the immediate site to prevent collisions with the unit by other vehicles.

3. A tie-down anchoring system designed by a Florida registered professional engineer to meet the wind up lift requirements of the Florida Building Code.

4. Facility siting so that it does not diminish egress from the hospital and so that the exhaust from the tractor and/or generator is kept away from all fresh air intakes of the hospital.

5. A rain-free covered passage from the hospital to the entrance of the mobile facility.

(b) Architectural Design Requirements:

1. An operating room with a minimum area of 170 square feet. The minimum room dimension shall be 12 feet.

2. An operating room service area containing sterilizing facilities, medication preparation and storage areas, scrub facilities, soiled work room with work counter, clean work room with storage for clean and sterile supplies, and janitor's closet with floor receptor or service sink.

3. A recovery room/Post-Anesthetic Care Unit (PACU) adjacent to the operating room, that shall accommodate two or more recovery beds. The size of this room shall be based on 80 square feet per recovery bed.

4. A nurse station for charting, communications, and storage.

5. A recovery service area containing a nourishment station, a hand washing facility, medication preparation area with refrigerator and double locked storage, clean linen storage, soiled linen area with soiled linen receptacles, and clean work area with work counter and sink.

6. An accessible patient/staff toilet room and hand wash facility adjacent to the recovery room.

7. A clothing change area for doctors, nurses and other personnel with secured storage and access to toilet room.

(c) Mechanical System Requirements:

1. The Heating, Ventilating and Air Conditioning systems shall be in compliance with NFPA 90A, incorporated by reference in the Florida Fire Prevention Code adopted by the State Fire Marshal and described in Rule Chapter 69A-60, F.A.C.

2. The patient gas medical systems shall be Type I as defined by NFPA 99, incorporated by reference in the Florida Fire Prevention Code adopted by the State Fire Marshal and described in Rule Chapter 69A-60, F.A.C. Medical gas, vacuum, and oxygen supply systems shall be in compliance with the requirements of NFPA 99, incorporated by reference in the Florida Fire Prevention Code adopted by the State Fire Marshal and described in Rule Chapter 69A-60, F.A.C.

3. The facility shall provide no fewer than the quantity of station outlets per bed position indicated in the following table:

Area	Oxygen 		Vacuum

Recovery room/(PACU)	1			3

Operating Room	2 			3

An additional vacuum station outlet shall be provided in the operating room dedicated for connection of an anesthesia machine.

4. The plumbing systems shall be in compliance with the Florida Building Code – Plumbing adopted by the Florida Building Commission and described in Rule 61G20-41.001, F.A.C.

5. The facility shall be equipped with fire extinguishers.

(d) Electrical System Requirements:

1. An essential electrical system which complies with a Type I system as defined in NFPA 99, incorporated by reference in the Florida Fire Prevention Code adopted by the State Fire Marshal and described in Rule Chapter 69A-60, F.A.C.

2. An electrical system which complies with Article 517 of the National Electric Code, NPFA 70, incorporated by reference in the Florida Fire Prevention Code adopted by the State Fire Marshal and described in Rule Chapter 69A-60, F.A.C, and with the Florida Building Code, adopted and described in Rule 61G20-41.001, F.A.C.

3. An automatic fire alarm system in the facility. An alarm initiated in the mobile facility shall activate the hospital fire alarm system and an alarm in the hospital shall initiate an alarm in the mobile facility.

4. A telephone connected to the hospital communication system.

5. Electrical connections to the hospital shall not interrupt, diminish or otherwise affect adversely in any way the electrical system of the hospital.

6. A lightning protection system as defined in NFPA 780, incorporated by reference in the Florida Fire Prevention Code adopted by the State Fire Marshal and described in Rule Chapter 69A-60, F.A.C., for the rain-free covered connection and the mobile facility, unless the mobile facility is shown to be within the cone of protection of the hospital and bonded to the lightning protection systems of the hospital.

(e) Details and Finishes: The mobile facility shall comply with the building codes in Rule 61G20-1.001, F.A.C.; as adopted by the Florida Building Commission.

Rulemaking Authority 395.0163, 395.1055 FS. Law Implemented 395.0163, 395.1055 FS. History–New 1-1-77, Formerly 10D-28.81, Amended 1-16-87, 11-23-88, Formerly 10D-28.081, Amended 9-3-92, 6-29-97, 3-18-98, 11-29-99, 12-20-99, 5-25-00, 5-12-16.