- 64B16-27.797 The Standards of Practice for Compounding Sterile Products.

The purpose of this section is to assure positive patient outcomes through the provision of standards for 1) pharmaceutical care; 2) the preparation, labeling, and distribution of sterile pharmaceuticals by pharmacies, pursuant to or in anticipation of a prescription drug order; and 3) product quality and characteristics. These standards are intended to apply to all sterile pharmaceuticals, notwithstanding the location of the patient (e.g., home, hospital, nursing home, hospice, doctor’s office, or ambulatory infusion center).

(1) Adoption of the United States Pharmacopeia: Beginning on October 1, 2014, all sterile compounding shall be performed in accordance with the minimum practice and quality standards of the following chapters of the United States Pharmacopeia (USP):

(a) Chapter 797, Pharmaceutical Compounding-Sterile Preparations;

(b) Chapter 71, Sterility Tests;

(c) Chapter 85, Bacterial Endotoxins Test;

(d) Chapter 731, Loss on Drying.

All referenced chapters of the USP, in subsection (1), are specifically referring to the United States Pharmacopeia, 36th revision, Second Supplement, which is hereby incorporated and adopted by reference with the effective chapter dates of December 1, 2013. A subscription to all relevant chapters is available for purchase at www.uspnf.com. The Board has determined that posting the incorporated material on the Internet would constitute a violation of federal copyright law. At the time of adoption, the copyrighted incorporated material will be available for public inspection and examination, but may not be copied, at the Department of Health, 4052 Bald Cypress Way, Tallahassee, Florida 32399-3254, and at the Department of State, Administrative Code and Register Section, Room 701, The Capitol, Tallahassee, Florida 32399-0250.

(2) Minimum Standards: The minimum practice and quality standards of the USP are adopted as the minimum standards to be followed when sterile products are compounded. However, nothing in this rule shall be construed to prevent the compounding of sterile products in accordance with standards that exceed the USP.

(3) Current Good Manufacturing Practices: The Board deems that this rule is complied with for any sterile products that are compounded in strict accordance with Current Good Manufacturing Practices per 21 U.S.C. §351 (2012), adopted and incorporated herein by reference, available at https://www.flrules.org/Gateway/reference.asp?No=Ref-04436 and 21 C.F.R. Parts 210 and 211 (2013), adopted and incorporated herein by reference, available at http://www.flrules.org/Gateway/reference.asp?No=Ref-04437.

(4) Registered Outsourcing facilities: For any pharmacy registered as an outsourcing facility, the minimum standards of practice for sterile compounding shall be the current good manufacturing practices as adopted in subsection (3).

(5) Clarifications, Variances, or Exceptions to the United States Pharmacopeia:

(a) Although the USP requires the donning of gloves prior to entry into the clean-room, all required donning of gloves can be performed after entry into the clean-room to avoid contamination of the gloves from the door handle or access device leading into the clean-room.

(b) USP Chapter 797 requires that: “When closed-system vial-transfer devices (CSTDs) (i.e., vial-transfer systems that allow no venting or exposure of hazardous substance to the environment) are used, they shall be used within an ISO Class 5 (see Table 1) environment of a BSC or CACI. The use of the CSTD is preferred because of their inherent closed system process. In facilities that prepare a low volume of hazardous drugs, the use of two tiers of containment (e.g., CSTD within a BSC or CACI that is located in a non-negative pressure room) is acceptable.” For purpose of said provision, a “low volume of hazardous drugs” is defined as less than 40 doses per month.

(c) USP Chapter 797 provides as follows in the “Facility Design and Environmental Controls” section: “An ISO Class 7 (see Table 1) buffer area and ante-area supplied with HEPA-filtered air shall receive an ACPH of not less than 30. The PEC is a good augmentation to generating air changes in the air supply of an area but cannot be the sole source of HEPA-filtered air. If the area has an ISO Class 5 (see Table 1) recirculating devise, a minimum of 15 ACPHs through the area supply HEPA filters is adequate, providing the combined ACPH is not less than 30. More air changes may be required, depending on the number of personnel and processes. HEPA-filtered supply air shall be introduced at the ceiling, and returns should be mounted low on the wall, creating a general top-down dilution of area air with HEPA-filtered make-up air. Ceiling-mounted returns are not recommended.” Notwithstanding the quoted provision, pharmacies that meet the standards set forth in the section quotes as of the effective date of this rule are not required to change the location of supply air or return filters or ducts so long as the ISO standards are maintained.

(d) USP Chapter 797 provides in part that the compounding facility’s ceiling tiles located in the ante-area, buffer area, and clean room that consist of inlaid panels “shall be impregnated with a polymer to render them impervious and hydrophobic, and they shall be caulked around each perimeter to seal them to the support frame.” A pharmacy shall not be required to caulk the inlaid ceiling tiles to the perimeter of the support frame if the following are met:

1. The ceiling tiles are specifically manufactured to be utilized in a facility that must meet and maintain an airborne particulate cleanliness of ISO Class 7 or better.

2. The core of the ceiling tiles are sealed on the front, back, and all edges to render them impervious and hydrophobic, so they can be properly maintained and cleaned as required by this rule.

3. The ceiling tiles are inlaid or installed using a gasket grid sealing system, which is manufactured for use in facilities that must meet and maintain an airborne particulate cleanliness of ISO Class 7 or better. The sealing system must create and maintain a positive seal between the ceiling tiles and the support frame and the seal between the ceiling tiles and support frame shall be secured with retention clips.

Rulemaking Authority 465.005, 465.0155, 465.022 FS. Law Implemented 465.0155, 465.022 FS. History–New 6-18-08, Amended 1-7-10, 10-1-14, 12-18-16.