- 62-761.800 Out-of-Service and Closure Requirements.

(1) Out-of-service storage tank systems.

(a) Storage tank systems that are taken out-of-service, as required in this subsection, shall continue to be maintained in accordance with this chapter unless otherwise noted herein.

(b) Facility owners and operators of out-of-service storage tank systems shall:

1. Continue to operate and maintain corrosion protection in accordance with subsection 62-761.700(2), F.A.C.,

2. Continue to maintain and demonstrate financial responsibility pursuant to rule 62-761.420, F.A.C.,

3. Leave vent lines open and functioning,

4. Remove all regulated substances so that no more than one inch in depth or 0.3 percent by weight of regulated substances remains in the storage tank; and,

5. Secure or close off the system to outside access.

(c) Facility owners and operators of out-of-service storage tank systems shall monitor the interstice and the liquid level in the storage tank annually but not to exceed 12 months, unless the tank system contains no regulated substances. Records of these inspections shall be maintained in accordance with subsection 62-761.710(2), F.A.C. In the event that liquid in excess of one inch, or 0.3 percent by weight, in the storage tank or any liquid, other than condensate, in the interstice is discovered, facility owners and operators must follow the procedures for incidents pursuant to rule 62-761.430, F.A.C.

(d) Release detection device annual operability testing, containment and interstitial integrity testing, and annual overfill protection device testing are not required while the system is properly out-of-service. All aforementioned testing shall be up-to-date in accordance with this chapter and indicate proper operation before adding regulated substances to the storage tank system. In addition, storage tank systems installed after January 11, 2017, that have been out-of-service for more than 730 days shall perform interstitial integrity testing of the storage tank and integral piping before adding regulated substances to the storage tank system.

(e) Storage tank systems with secondary containment shall only be designated as out-of-service for a maximum of 10 continuous years. Upon expiration of this time period, the storage tank system must be closed in accordance with subsection 62-761.800(2)(b), F.A.C.

(2) Closure of storage tank systems.

(a) The following storage tank systems must be closed in accordance with the provisions of this subsection:

1. A storage tank system that fails to meet or, if required, is not modified to meet the Storage Tank System Requirements of Rule 62-761.500, F.A.C., within 90 days of discovery.

2. A storage tank system that requires repair pursuant to rule 62-761.700, F.A.C., but cannot be repaired to operate in accordance with the requirements of this chapter shall be taken out-of-service. If it cannot be repaired within 365 days after being taken out-of-service, it shall be permanently closed.

3. A storage tank system where financial responsibility is not maintained and demonstrated, pursuant to rule 62-761.420, F.A.C., within 90 days of termination of the financial mechanism.

(b) Closure of storage tank systems shall be performed by:

1. Conducting a Closure Integrity Evaluation as defined in subsection 62-761.200(10), F.A.C., and completing the Closure Integrity Evaluation Report Form for USTs 62-761.900(7) (Closure Integrity Report), incorporated by reference in paragraph 62-761.405(2)(c), F.A.C. The form shall be submitted in writing or electronic format to the appropriate county,

2. Removing all liquids and accumulated sludges. The removal and disposal of all liquids and accumulated sludges may be required according to other local, state, and federal requirements,

3. Removing by a Certified Contractor or disconnecting and capping all integral piping,

4. Removing and disposing of a storage tank by a Certified Contractor, or in-place closure by filling the storage tank with a solid inert material of sufficient density to prevent a structural collapse of the closed storage tank, which shall be in accordance with the following documents, hereby adopted and incorporated by reference, and available from the addresses given, regardless of the date of installation of the storage tank system: Closure of Underground Petroleum Storage Tanks, API Recommended Practice 1604, 3rd Edition, March 1996 (Reaffirmed, November 2001), available at the Department address listed in subsection 62-761.210(1), F.A.C., or from the publisher at API, 1220 L Street, N.W. Washington, DC 20005, (202)682-8000, or the publisher’s website at http://www.api.org/; and Temporarily Out of Service, Closure in Place, or Closure by Removal of Underground Storage Tanks, NFPA 30 (Annex C), 2015 Edition, available at the Department address listed in subsection 62-761.210(1), F.A.C., or from the publisher at NFPA, 1 Batterymarch Park, Quincy, Massachusetts 02169-7471, (800)344-3555, or at the publisher’s website at www.nfpa.org/. In lieu of in-place closure or removal, a storage tank may be used to store liquids other than regulated substances in accordance with API Recommended Practice 1604, 3rd Edition, March 1996 (Reaffirmed, November 2001). Owners and operators are advised that other federal, state, or local requirements apply that regulate these activities; and,

5. Properly closing monitoring wells associated with closed systems that are not being used for site assessment purposes.

(3) Closure Integrity Report, Closure Report, and Limited Closure Report Requirements.

(a) Closure Integrity Report.

1. A Closure Integrity Evaluation, as defined in subsection 62-761.200(10), F.A.C., must be performed no more than 45 days prior to closure, replacement, or change in service from a regulated substance to a non-regulated substance for all double-walled storage tanks, double-walled integral piping, piping sumps, dispenser sumps, and spill containment systems that are in contact with the soil. A Closure Integrity Report must be completed to document the findings of the Closure Integrity Evaluation.

2. A Closure Integrity Evaluation requires a visual assessment of the interstitial space of double-walled tanks, integral piping, piping sumps, dispenser sumps, and spill containment systems that are in contact with the soil to determine if there are any products or pollutants or any water other than condensate present within the interstice. Other methods approved by the manufacturer or the Department such as vacuum, pressure, or inert gases may be used instead of visual observations.

3. A Closure Integrity Evaluation for single-walled piping sumps, dispenser sumps, and spill containment systems that are in contact with the soil requires a hydrostatic test or another test approved by the manufacturer.

4. The county must be provided with a copy of the Closure Integrity Report as part of the notification process pursuant to subsection 62-761.405(2), F.A.C.

5. A failed Closure Integrity Evaluation requires the reporting of the failed evaluation as an incident in accordance with subsection 62-761.405(3), F.A.C., and the investigation of the incident in accordance with subsection 62-761.430, F.A.C. If sampling is necessary to determine whether a discharge has occurred, then an investigation shall be conducted during closure in accordance with Instructions for Conducting Sampling During Underground Storage Tank Closure, April 2016 Edition, hereby adopted and incorporated by reference, and available at http://www.flrules.org/Gateway/reference.asp?No=Ref-07662, or the Department address given in paragraph 62-761.210(1)(e), F.A.C., or the Department’s website at https://floridadep.gov/waste/permitting-compliance-assistance/content/storage-tank-system-rules-forms-and-reference, regardless of the date of installation of the storage tank system or system component being closed.

6. The owner or operator who does not conduct a Closure Integrity Evaluation before the storage tank system or system component has been removed or closed in-place, regardless of the date of installation of the storage tank system or system component, shall conduct an investigation at the time of closure in accordance with Instructions for Conducting Sampling During Underground Storage Tank Closure, April 2016 Edition.

(b) Closure Report. In cases where an investigation is conducted at the time of closure in accordance with Instructions for Conducting Sampling During Underground Storage Tank Closure, April 2016 Edition, a Closure Report shall be submitted in writing or electronic format to the County within 60 days of completion of the closure, replacement, or change in service from a regulated substance to a non-regulated substance. The Closure Report shall be prepared in accordance with Instructions for Conducting Sampling During Underground Storage Tank Closure, April 2016 Edition.

(c) Limited Closure Report. In cases where a Closure Integrity Evaluation passed or where a failed Closure Integrity Evaluation was investigated prior to closure and it was demonstrated that a discharge did not occur, Form 62-761.900(8), Limited Closure Report Form for USTs, incorporated by reference in subsection 62-761.420(2), F.A.C., shall be submitted in writing or electronic format to the county within 60 days of completion of the closure, replacement, or change in service from a regulated substance to a non-regulated substance.

Rulemaking Authority 376.303 FS. Law Implemented 376.303, 376.0716 FS. History–New 12-10-90, Formerly 17-761.800, Amended 9-30-96, 7-13-98, 6-21-04, 1-11-17.