61C-5.0012 Electrolysis Protection for Underground Hydraulic Elevator Cylinders.

All newly installed underground hydraulic pressure cylinders shall be encased in an outer plastic containment to minimize electrolytic corrosion between the metal cylinder and ground cathode.

(1) The plastic casing shall be capped at the bottom, and all joints must be solvent or heat welded to insure water tightness.

(2) The plastic casing shall be constructed of polyethylene or polyvinyl chloride (PVC). The plastic pipe wall thickness must not be less than .125 inches (3.175 mm).

(3) The neck of the plastic casing shall have a means of inspection provided to monitor the annulus between the pressurized hydraulic cylinder and the protective plastic casing.

(4) Replacements of existing hydraulic cylinders shall be protected by the aforementioned method where existing physical dimensions permit.

Specific Authority 399.02 FS. Law Implemented 399.02 FS. History–New 9-10-89, Formerly 7C-5.0012.