61G15-32.003 Common Requirements to All Fire Protection Engineering Documents.

(1) The Fire Protection System Engineering Documents shall provide the engineering requirements to be used in the preparation of the Fire Protection System Layout Documents and to indicate the nature and scope of the work, and to describe, detail, dimension, label and define the Fire Protection Components, System(s), materials, assemblies, equipment and its structural and utility support system(s), insofar as they involve the safeguarding of life, health or property.

(2) The Fire Protection System Engineering Documents shall specify the applicable requirements for the acceptance testing of the fire protection system and components, which shall be based upon applicable codes and standards, where available.

(3) The occupancy of the area or description of a specific hazard being protected by the Fire Protection System(s) shall be shown on the Fire Protection System Engineering Documents.

(4) The applicable code and standard to be used in the preparation of the Fire Protection System Layout Documents shall be shown on the Fire Protection System Engineering Documents. When codes and standards are not available or applicable, and said layout documents are to be based on engineering judgment, any reasons and assumptions made to develop the fire protection concept shall be identified on the Fire Protection System Engineering Documents.

(5) Structural support and structural openings required by the Fire Protection System shall be shown on the Fire Protection System Engineering Documents and shall be referenced on structural engineering documents.

(6) When layout documents contain material deviation from the Engineer of Record’s Fire Protection System Engineering Document, such layout documents are not compliant unless they are accompanied by revised Engineering Documents made and sealed by the Engineer of Record for the Fire Protection System.

(7) Requirements for activation control systems, sequence, operating parameters, interlocks, safety related devices, indicators and alarms, shall be shown on the Fire Protection System Engineering Documents, unless shown on other related documents.

(8) Any information deemed appropriate by the Engineer of Record to assist the authority having jurisdiction in understanding the owner’s intended use and proposed protection of the building or facility and to provide sufficient direction to the installation contractor or other interested parties regarding the layout of the system(s), shall be included in the Fire Protection System Engineering Documents.

Specific Authority 471.008, 471.033(2) FS. Law Implemented 471.005(7), 471.033(2) FS. History–New 5-19-93, Formerly 21H-32.003, Amended 4-2-00, 6-26-01.