61G15-33.003 Design of Power Systems.

(1) Power systems convey or distribute electrical energy. Items to be included in the design and analysis of these systems are: steady state and transient loads, short circuit analysis and protection (design and analysis), load flow, voltage drop, harmonics and protective device coordination.

(2) Electrical Engineering Documents applicable to power systems shall at a minimum indicate the following:

(a) Power Distribution Riser Diagram with short circuit values.

(b) Conductor Ampacities (sizes) and insulation type.

(c) Circuit interrupting devices and fault current interrupting capability.

(d) Location and characteristics of surge protective devices.

(e) Main and distribution equipment, control devices, locations and sizes.

(f) Voltage drop calculations for the feeders and customer-owned service conductors are required. Additionally, the documents shall state the reasons why the two percent limit for feeders and customer-owned service conductors are not being met, if applicable.

(g) Circuitry of all outlets, equipment and devices.

(h) Load computations.

(i) Electrical legends.

(j) Grounding and bonding.

(k) Instrumentation and control where required.

(l) Record documents applicable to power systems shall, at a minimum, contain information as required by Florida Building Code.

(m) Installation and testing requirements of required emergency and standby power systems.

Specific Authority 471.008, 471.033(2) FS. Law Implemented 471.033 FS. History–New 5-19-93, Formerly 21H-33.003, Amended 11-13-08.