61G15-34.003 Design of Heating Ventilation and Air Conditioning Systems.

(1) Heating, Ventilating, and Air Conditioning (HVAC) Systems are those systems that control the temperature and/or humidity of a particular space or building. Items to be considered in the design and analysis of these systems are ambient dry and wet bulb temperatures, inside dry and wet bulb temperatures, inside design humidity, fresh air makeup, internal heat gains from any sources. Ventilation systems shall be designed to remove foul odors from a space or building, or to remove space heat from equipment rooms. All HVAC systems shall be designed in accordance with the ASHRAE Standards and Building Code as adopted by the authority having jurisdiction. The HVAC systems shall be designed and operated such that the entire building is under positive or neutral pressure when all primary HVAC systems are operating.

(2) Mechanical Engineering documents applicable to HVAC systems shall, where applicable, include but are not limited to the following:

(a) Equipment selection schedule for each piece of mechanical equipment. All equipment shall have capacities listed including efficiencies, electrical or fuel requirements, static pressure and fan air quantities as applicable to the system, fluid flow and pressure head quantities as applicable to the system, and heat transfer capacities.

(b) Floor plans; site plans; and building and mechanical system elevations as appropriate.

(c) Outside (fresh) air make-up conditions.

(d) Cooling coil requirements based on sensible heat, latent heat and total heat gains.

(e) Heating equipment requirements.

(f) Outside and inside design dry and wet bulb conditions.

(g) Exhaust riser diagrams.

(h) Outside air riser diagrams.

(i) Process flow diagrams with pipe sizes and fluid flow quantities.

(j) Condensate discharge piping with pipe sizes.

(k) Instrumentation and Control System diagrams and sequence of operation.

(l) Ductwork layout and sizing; insulation, supply, return, and exhaust inlet and outlet sizes; and outside air intake sizes. Air quantities shall be specified for inlets and outlets.

(m) Florida Energy Code calculations as applicable.

(n) NFPA Standards and all required fire protection devices and systems.

Specific Authority 471.008, 471.033(2) FS. Law Implemented 471.033 FS. History–New 11-16-94.