62-601.500 Sampling Schedules, Locations, and Methodology.

(1) Sampling schedules for parameters to be monitored by wastewater facilities shall be included in the wastewater facility permit.

(2) The minimum schedule for sampling and testing parameters to be monitored at a wastewater treatment plant is specified in Figure 2. Ground water monitoring wells shall be tested according to the schedule specified in Figure 3.

(3) Sampling methodology (time, period, location) for grab and composite samples may be specified in the permit, if deemed necessary, for the purpose of obtaining representative samples.

(a) Grab samples shall be used to test pH, chlorine residual, dissolved oxygen, and fecal coliforms.

(b) Grab samples may be used to test for suspended solids at facilities with flows less than 100,000 gallons per day. Where a facility is required to meet the 5.0 mg/L TSS limitation associated with high-level disinfection, grab samples shall be required. All other samples for suspended solids testing shall be flow proportioned, composite samples. Where Chapter 62-602, F.A.C., requires a Class A, B, or C operator, 24, 16, or 8 hour compositing periods are required, respectively.

(c) Grab samples may be used to test CBOD5 and nutrients at facilities with flows less than 100,000 gallons per day. All other facilities shall use flow proportioned composite samples to test CBOD5 and nutrients. Where Chapter 62-602, F.A.C., requires a Class A, B, or C operator, 24, 16, or 8 hour compositing periods are required, respectively.

(d) Twenty-four hour composite samples shall be used to analyze reclaimed water or effluent for the primary and secondary drinking water standards.

(4) Sampling locations which are different from or are not specified by Rule 62-601.500, F.A.C., shall be specified in the permit for the treatment plant.

(a) Influent samples shall be collected so that they do not contain digester supernatant or returned activated sludge, or any other plant process recycled waters.

(b) Reclaimed water or effluent analyses shall generally be performed on samples collected after final treatment and:

1. Before discharge to holding ponds for reuse and land application systems pursuant to Chapter 62-610, F.A.C.;

2. After holding ponds, if applicable, and immediately before discharge to surface waters for treatment plants discharging to surface waters including overland flow systems and treatment wetland systems; and

3. After holding ponds, if applicable, and immediately before discharge to ground waters for treatment plants discharging to ground waters via underground injection.

(c) For systems involving high-level disinfection, compliance with the TSS limitation shall be achieved, and sampled for, after the filter and before application of the disinfectant.

(5) Wastewater treatment facilities shall provide safe access points for obtaining representative influent and effluent samples which are required by this chapter.

(6) Recording flow meters and totalizers shall be required to measure flows of 100,000 gallons per day or greater. Flow recording devices shall be calibrated on an annual basis.

Specific Authority 403.051, 403.061, 403.088 FS. Law Implemented 403.051, 403.061(13), 403.088 FS. History–New 1-1-75, Amended 6-10-76, Formerly 17-19.05, 17-19.050, Amended 1-30-91, 5-31-93, Formerly 17-601.500, Amended 12-24-96.