62-602.650 Duties of Operators.

An operator is responsible for performing treatment plant operation and maintenance duties in a responsible and professional manner consistent with standard operating practices. The duties shall be the following:

(1) Perform responsible and effective on-site management and supervision over personnel and plant functions including, if applicable, reuse and disposal systems within the operator’s responsibility.

(2) Submit all required reports in the manner required by the Department in Rule 62-601.300 or 62-550.730, F.A.C., to the permittee or supplier of water.

(3) Report to the permittee or supplier of water and the Department and, if applicable, the local regulatory agency, as soon as possible, but within 24 hours following the discovery of any serious plant breakdown or condition causing or likely to cause:

(a) Unsafe treatment plant operation, or

(b) Any discharge of water or wastewater not in accordance with Chapters 62-550, 62-555 and 62-302, F.A.C., or the facility’s permit, or

(c) Any major interruption in service.

(4) Maintain operation and maintenance logs for each plant, on site in a location accessible to 24-hour inspection, protected from weather damage, and current to the last operation and maintenance performed. The logs shall be maintained in hard bound books with consecutive page numbering, and shall contain a minimum of the previous three months of data at all times. Alternative logs or partial electronic logging are acceptable if approved by the appropriate Department district office or the local regulatory agency. The logs shall contain:

(a) Identification of the plant;

(b) The signature and license number of the operator and the signature of the persons making any entries;

(c) Date and time in and out;

(d) Specific operation and maintenance activities and any repairs made;

(e) Results of tests performed and samples taken, unless documented on a laboratory sheet.

(f) Performance of preventive maintenance and repairs or requests for repair of the equipment.

Specific Authority 403.869 FS. Law Implemented 403.865, 403.875(1)(a) FS. History–New 12-30-99, Amended 2-6-02.