62-761.510 Performance Standards for Category-A and Category-B Storage Tank Systems.

(1) General. This section provides deadlines for Category-A and Category-B storage tank systems to meet the standards for Category-C storage tank systems in accordance with Rule 62-761.500, F.A.C.

(a) Installation:

1. Installation shall be completed by the deadlines specified in Table UST. However, if installation or upgrade activities are initiated before the deadlines, work can continue after the deadlines, provided that all work is completed within 90 days of:

a. Contract execution; or

b. Receipt of construction approval or permits.

2. Installation is considered to have begun if:

a. All federal, state, and local approvals or permits have been obtained or applied for to begin physical construction for installation of the system; or

b. Contractual obligations have been made for installation of the system which cannot be cancelled or modified without substantial economic loss, provided that such obligations are pursued diligently in good faith to achieve the requirements of this rule.

(b) By December 31, 1998:

1. All pressurized small diameter piping systems connected to dispensers shall have shear valves or emergency shutoff valves installed in accordance with paragraph 62-761.500(8)(c), F.A.C.

2. Cathodic protection test stations shall be installed in accordance with subparagraphs 62-761.500(1)(e)1. and (2)(b)2., F.A.C., for cathodically protected UST systems without test stations.

3. Fillboxes shall be color coded in accordance with paragraph 62-761.500(5)(a), F.A.C.

4. ASTs that have been reinstalled as USTs, shall meet the requirements of Rule 62-761.500, F.A.C.

(c) After July 13, 1998, a closure assessment shall be performed in accordance with subsection 62-761.800(3), F.A.C., before the installation of dispenser liners, piping sumps, or secondary containment of tanks and integral piping.

(d) Valves meeting the requirements of Section 2-1.7 of NFPA 30A, shall be installed by January 13, 1999 on any storage tank system located at an elevation that produces a gravity head on the dispenser or on small diameter piping.

(e) Small diameter piping transporting regulated substances over surface waters of the state shall have secondary containment by December 31, 2004.

(2) UST Category-A single-walled tanks or underground single-walled piping shall be considered to be protected from corrosion if the tank or piping was constructed with corrosion resistant materials, initially installed with cathodic protection, or had cathodic protection or internal lining installed before June 30, 1992.

(3) UST Category-B systems.

(a) All tanks containing pollutants, installed or constructed at a facility after June 30, 1992, shall have secondary containment.

(b) All tanks containing hazardous substances, installed or constructed at a facility after January 1, 1991, shall have secondary containment.

(4) Small diameter integral piping in contact with the soil that is connected to UST systems shall have secondary containment if installed after December 10, 1990.

(5) By December 31 of the appropriate year shown in Table UST below, all storage tank systems shall meet the performance standards of Rule 62-761.500, F.A.C., or be permanently closed in accordance with subsection 62-761.800(2), F.A.C.

| TABLE UST |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Year Tank or |  |  |  |  |  |  |
| Integral Piping |  |  |  |  |  |  |
| Installed | 1989 | 1992 | 1995 | 1998 | 2004 | 2009 |
| +Before 1970 | O | B |  | ACFL | D | E |
| +1970-1975 |  | SBL |  | ACF | D | E |
| +1976-1980 |  | B | SL | ACF | D | E |
| +1981-09/01/84 |  | B |  | ACFL | D | E |
| +09/02/84-06/30/92 |  | B |  | ACFL | D | E |
| +Other* |  | B |  | ACFL | D | E |

Key to Table UST

* = All systems with a capacity of between 110 gallons and 550 gallons, all marine fueling facilities as defined in Section 376.031, F.S., and those systems of greater than 550 gallon capacity that use less than 1,000 gallons per month or 10,000 gallons per year.

A =

(1) Small diameter piping that was protected from corrosion by June 30, 1992, shall have:

(a) For pressurized piping, line leak detectors with automatic shutoff, or flow restriction in accordance with paragraph 62-761.640(4)(a), F.A.C.; or

(b) For suction integral piping:

1. Secondary containment in accordance with paragraph 62-761.500(1)(d), F.A.C.;

2. A single check valve installed in accordance with subparagraph 62-761.610(3)(a)3., F.A.C.;

3. An annual line tightness test in accordance with subparagraph 62-761.610(3)(a)1., F.A.C.; or

4. External monthly monitoring or release detection in accordance with sub-subparagraph 62-761.610(3)(a)1.b., F.A.C.

(2) Bulk product piping in contact with soil shall be upgraded with secondary containment unless the piping is:

(a) Constructed of corrosion resistant materials or upgraded with cathodic protection; and

(b) Tested on an annual basis in accordance with API RP 1110, ASME B31.4, or an equivalent method approved by the Department in accordance with Rule 62-761.850, F.A.C.

B = Vehicular fuel petroleum storage tank systems shall be upgraded with spill containment.

C = Secondary containment in accordance with paragraph 62-761.500(1)(d), F.A.C., shall be required for the following:

(1) Concrete storage tanks;

(2) Hazardous substance storage tank systems; and

(3) For pollutant storage tank systems, the storage tank or small diameter piping not protected from corrosion by June 30, 1992.

D = (1) Secondary containment shall be installed for small diameter piping extending over surface waters.

(2) Secondary containment for remote fill-pipes associated with Category-A and Category-B systems.

E = Pollutant storage tanks and small diameter piping protected from corrosion on or before June 30, 1992, and all manifolded piping, shall be upgraded with secondary containment.

F = (1) Storage tank systems, excluding vehicular fuel petroleum storage tank systems, shall be upgraded with spill containment, dispenser liners (as applicable), and overfill protection.

(2) Unless contained within secondary containment, swing-joints and flex-connectors that are not protected from corrosion shall be protected from corrosion. Facilities that have pressurized small diameter piping and that have not met the foregoing standard on or before July 13, 1998 shall protect the submersible turbine pump from corrosion or provide corrosion protection for the submersible turbine pump if the pump is not installed within secondary containment. Corrosion protection is not required for the submersible turbine pump riser.

L = (1) Category-A USTs and their integral piping systems that contain vehicular fuel, and that are not protected from corrosion, shall have secondary containment, or be upgraded with secondary containment in accordance with Rule 62-761.500, F.A.C.

(2) Dispenser liners and overfill protection equipment shall be installed at UST Category-A systems containing vehicular fuel.

O = UST Category-A vehicular fuel storage tank systems subject to Chapter 17-61, F.A.C., (1984), shall be retrofitted for corrosion protection.

S = Secondary containment for storage tanks and integral piping not protected from corrosion.

Specific Authority 376.303 FS. Law Implemented 376.303-.3072 FS. History–New 12-10-90, Amended 5-4-92, Formerly 17-761.510, Amended 9-30-96, 7-13-98, 6-21-04.