62-761.610 Release Detection Methods.

(1) General.

(a) Category-A and Category-B systems. Release detection methods shall be one of the methods specified in this section, and shall meet the performance standards contained in Rule 62-761.640, F.A.C.

(b) Category-C systems. Release detection methods shall be either interstitial or visual monitoring of secondary containment in accordance with Rule 62-761.640, F.A.C. Small diameter pressurized piping shall have a line leak detector in accordance with paragraph 62-761.640(4)(a), F.A.C. A breach of integrity test shall be performed every five years for Category-C storage tank systems with closed interstitial spaces, unless the test is a continuous test.

(2) Category-A and Category-B USTs shall be equipped with one or more of the following release detection systems:

(a) An interstitial monitoring system between the walls of a double-walled tank;

(b) Interstitial monitoring involving a single monitoring well or vapor detector located within a liner that meets the standards in paragraph 62-761.500(1)(d), F.A.C., provided the well or detector is placed at the low point of the liner so that collected liquids will drain to the monitoring point;

(c) A continuously operating release detection system placed around a tank in an excavation or in the secondary containment in accordance with the manufacturer’s requirements;

(d) A network of groundwater or vapor monitoring wells installed or verified in accordance with paragraphs 62-761.640(2)(a)-(d), F.A.C., as applicable;

(e) Automatic tank guage systems.

1. An automatic tank gauge system with a tightness test of the storage tank every three years; or

2. A continuous automatic tank gauge system;

(f) A statistical inventory reconciliation system with a tightness test of the storage tank every three years;

(g) Manual tank gauging shall be performed as specified in Table MTG in paragraph 62-761.640(3)(c), F.A.C., for tanks of 550 gallons or less nominal capacity, and for tanks 551-1000 gallons with known diameters of 48 or 64 inches;

(h) Manual tank gauging may be used for tanks of 551 to 2000 gallons nominal capacity provided that a tank tightness test is performed:

1. Every 12 months for tanks not protected from corrosion by June 30, 1992; or

2. Every five years for tanks installed with corrosion protection, or for tanks upgraded with corrosion protection by June 30, 1992. However, this method is only available for the first 10 years after:

a. A tank is upgraded with cathodic protection;

b. A single-walled corrosion-protected tank is installed; or

c. Until December 22, 1998, whichever is later;

(i) An annual tank test in conjunction with inventory control performed in accordance with Rule 62-761.640, F.A.C. This method can only be used until:

1. Ten years after the date of installation of a single-walled corrosion protected tank;

2. Ten years after the tank is upgraded with corrosion protection or internal lining; or

3. December 22, 1998, whichever is later.

(3) Integral piping.

(a) Small diameter piping in contact with the soil. Single-walled piping that is in contact with soil shall be equipped with one of the following release detection systems:

1. Suction or gravity piping shall have:

a. An annual line tightness test; or

b. An external monthly monitoring or release detection method meeting the requirements of subsection 62-761.640(2), F.A.C., if designed to detect a discharge from any portion of the integral piping.

2. By December 31, 1998, pressurized piping shall have:

a. Mechanical line leak detectors meeting the requirements of paragraph 62-761.640(4)(a), F.A.C., and either an annual line tightness test, or an external release detection method meeting the requirements of paragraphs 62-761.640(2)(a)-(d), F.A.C.; or

b. Electronic line leak detectors meeting the requirements of paragraph 62-761.640(1)(a), F.A.C.

3. Exemptions. Release detection is not required for piping associated with:

a. Suction pumps, provided that a single check valve is installed directly below the suction pump, and the piping is sloped so that the contents of the pipe will drain back to the tank if the suction is broken. Written verification shall be provided by a certified contractor that no other check valves exist between the dispenser and the tank, and that the above criteria are met. Any subsequent modification of the piping which involves disconnection shall be recertified by a Certified Contractor that these conditions are still being met; and

b. Manifold piping systems.

(b) Small diameter piping not in contact with the soil, or that is exempt from secondary containment. These systems shall be visually inspected in accordance with paragraph 62-761.640(2)(e), F.A.C.

(c) Small diameter piping with secondary containment that is in contact with the soil. Double-walled piping, or single-walled piping with secondary containment shall be equipped with the following release detection systems:

1. Interstitial monitoring;

2. A method of testing for a breach of integrity that meets the requirements of subparagraph 62-761.640(3)(a)2., F.A.C., for Category-C systems, as applicable; and

3. A line leak detector that restricts or shuts off flow or a continuously operating interstitial monitoring device that meets the requirements of subparagraph 62-761.640(4)(a)5., F.A.C., for pressurized piping connected to a UST, by December 31, 1998.

(d) Bulk product and hyrant piping.

1. Single-walled piping in contact with the soil:

a. Shall be pressure tested annually in accordance with paragraph 62-761.640(5)(a), F.A.C.; or

b. Instead of annual testing, a monthly release detection system meeting the requirements of subsection 62-761.640(2) F.A.C., may be installed.

2. Piping not in contact with the soil, or that is exempt from secondary containment, shall be visually inspected in accordance with paragraph 62-761.640(2)(e), F.A.C.

3. Piping with secondary containment that is in contact with the soil, such as double-walled piping or single-walled piping with secondary containment, shall be equipped with the following release detection systems:

a. Interstitial monitoring; and, if applicable,

b. For Category-C systems, a method of testing for a breach of integrity that meets the requirements of subparagraph 62-761.640(3)(a)2., F.A.C., for piping with closed interstitial spaces.

Specific Authority 376.303 FS. Law Implemented 376.303 FS. History–New 12-10-90, Formerly 17-761.610, Amended 9-30-96, 7-13-98, 6-21-04.