62-761.800 Out-of-Service and Closure Requirements.

(1) Out-of-service storage tank systems.

(a) General.

1. Storage tank systems that are taken out-of-service, as defined in subsection 62-761.200(40), F.A.C., shall:

a. Continue to operate and maintain corrosion protection in accordance with paragraph 62-761.700(1)(b), F.A.C.;

b. Perform external release detection for sites without contamination, as applicable, every six months in accordance with provisions of subsection 62-761.640(2), F.A.C.;

c. Leave vent lines open and functioning;

d. Empty the system and cap or secure all lines, pumps, manways, and ancillary equipment, as applicable; and

e. Secure or close off the system to outside access.

2. If the storage tank system is required to be upgraded during the time that it is out-of-service, it shall be upgraded or replaced in accordance with this chapter before it is returned to service.

3. Systems with secondary containment installed and operated in accordance with this chapter may remain in a continuous out-of-service status for ten years. After this period, the system shall be returned to service or closed in accordance with subsection 62-761.800(2), F.A.C.

4. Tightness, pressure, or other tests shall be performed in accordance with subsection 62-761.640(3), F.A.C., as applicable, on any systems being returned to service.

(b) Before being returned to service, the following tests shall be performed in accordance with subsection 62-761.640(3), F.A.C., for systems that are taken out-of-service for more than 180 days:

1. A tightness test for single-walled systems; or

2. A breach of integrity test for double-walled Category-C systems.

(c) Single-walled systems that are taken out-of-service shall not be kept out-of-service longer than two years for corrosion-protected systems or one year for unprotected bare steel systems. After the end of these time periods, the systems shall either be upgraded or permanently closed.

(2) Closure of storage tank systems.

(a) General.

1. Closure of storage tank systems shall be performed by:

a. Removing all liquids and accumulated sludges;

b. Disconnecting and capping, or removing, all integral piping. Manways shall be secured to prevent access;

c. Closing the storage tank system in accordance with paragraphs 62-761.800(2)(b), F.A.C., as applicable; and

d. Conducting a closure assessment in accordance with subsection 62-761.800(3), F.A.C.

2. After closure, storage tank systems may be used to store materials or substances other than regulated substances in accordance with all applicable Department reference standards, (for example, API 1604). Owners and operators are advised that other federal, state, or local requirements may apply to these activities.

3. Monitoring wells associated with closed systems that are not being used for release detection or site assessment purposes shall be closed in accordance with paragraph 62-761.600(1)(k), F.A.C.

(b) Unmaintained systems shall be permanently closed within 90 days of discovery.

(c) System removal, closure in-place, and disposal shall be performed:

1. In accordance with API RP 1604 and NFPA 30; and

2. By a Certified Contractor if the system is removed from the ground, unless it is closed in place by filling it with a solid inert material of sufficient density to prevent a structural collapse of the closed system.

(3) Closure assessment of storage tank systems.

(a) At time of closure, replacement, installation of secondary containment, or change in service from a regulated substance to a non-regulated substance, an assessment shall be performed to determine if a discharge from the system or system components has occurred.

1. If a Site Rehabilitation Completion Order (SRCO) or a Monitoring Only Plan (MOP) Approval Order has been issued by the Department for a contaminated area of a site, a closure assessment shall be performed for any subsequent storage tank system removal, replacement, or installation of secondary containment.

2. Tanks, pipes, or other system components in contact with soil at any site are subject to closure assessment requirements.

(b) A closure assessment is not required for:

1. Sites with documented contamination requiring a site assessment in accordance with Chapter 62-770, F.A.C., including those that are eligible for the Early Detection Incentive Program (EDI), the Florida Petroleum Liability and Restoration Insurance Program (FPLRIP), and the Petroleum Cleanup Participation Program (PCPP), pursuant to Sections 376.3071 and 376.3072, F.S. Nevertheless, documentation of procedures followed and results obtained during closure shall be reported in a Limited Closure Summary Report, Form 62-761.900(8), and in accordance with Section A of DEP’s “Storage Tank System Closure Assessment Requirements”;

2. Systems initially installed with secondary containment, provided that no unexplained positive response of an interstitial release detection device or method occurred during the operational life of the system, or the secondary containment passed a breach of integrity test prior to closure; and

3. Systems upgraded with secondary containment that have closed interstitial spaces, where a closure assessment was performed prior to installation of secondary containment, provided that the secondary containment passed a breach of integrity test in accordance with paragraph 62-761.640(3)(a), F.A.C.;

(c) Closure assessment sampling and analysis shall be conducted according to DEP’s “Storage Tank System Closure Assessment Requirements.”

(d) A closure assessment report shall be submitted to the County within 60 days of completion of any of the activities listed in paragraph 62-761.800(3)(a), F.A.C. The report shall include sample types, sample locations and measurement methods, a site map, methods of maintaining quality assurance and quality control, and any analytical results obtained during the assessment in accordance with DEP’s “Storage Tank System Closure Assessment Requirements.”

(e) Persons are advised that contaminated soil excavated, disposed of, or stockpiled on site during the closure of a storage tank system is regulated by Chapter 62-770, F.A.C.

Specific Authority 376.303 FS. Law Implemented 376.303 FS. History–New 12-10-90, Formerly 17-761.800, Amended 9-30-96, 7-13-98, 6-21-04.