62-762.511 Performance Standards for Category-A and Category-B Storage Tank Systems.

(1) General. This section provides deadlines for Category-A and Category-B storage tank systems to meet the standards for Category-C storage tank systems in accordance with Rule 62-762.501, F.A.C.

(a) Installation:

1. Installation shall be completed by the deadlines specified in Table AST. However, if installation or upgrade activities are initiated before the deadlines, work can continue after the deadlines, provided that all work is completed within 90 days of:

a. Contract execution; or

b. Receipt of construction approval or permits.

2. Installation is considered to have begun if:

a. All federal, state, and local approvals or permits have been obtained or applied for to begin physical construction for installation of the system; or

b. Contractual obligations have been made for installation of the system which cannot be canceled or modified without substantial economic loss, provided that such obligations are pursued diligently in good faith to achieve the requirements of this rule.

(b) By December 31, 1998:

1. All pressurized small diameter piping systems connected to dispensers shall have shear valves or emergency shutoff valves installed in accordance with paragraph 62-762.501(3)(c), F.A.C.

2. Cathodic protection test stations shall be installed in accordance with subparagraph 62-762.501(1)(f)1., F.A.C., for cathodically protected AST systems without test stations.

3. ASTs that have been reinstalled as USTs shall meet the requirements of Rule 62-762.501, F.A.C.

(c) After July 13, 1998, a closure assessment shall be performed in accordance with subsection 62-762.801(4), F.A.C., before the installation of dispenser liners, piping sumps, or secondary containment of tanks and integral piping.

(d) Valves meeting the requirements of Section 2-1.7 of NFPA 30A, shall be installed by January 13, 1999 on any storage tank system located at an elevation that produces a gravity head on the dispenser or on small diameter piping.

(e) Small diameter piping transporting regulated substances over surface waters of the state shall have secondary containment by December 31, 2004.

(2) Aboveground storage tank systems.

(a) All storage tank systems with tanks having capacities greater than 550 gallons that contain vehicular fuel and that were subject to Chapter 17-61, F.A.C., shall have met the requirements of such chapter by January 1, 1990.

(b) AST Category-B tanks, with the exception of tanks exempt under sub-subparagraph 62-762.501(2)(c)1.a., F.A.C., installed or constructed at a facility after March 12, 1991, shall have secondary containment for the tank.

(c) Integral piping that is in contact with the soil and that is connected to AST systems shall have secondary containment if installed after March 12, 1991. For integral piping that is exempt under subparagraph 62-762.501(3)(e)4., F.A.C., it is not required to install secondary containment.

(d) By January 1 of the appropriate year shown in Table AST below, unless specified otherwise, all AST Category-A and Category-B storage tank systems shall meet the following requirements or be permanently closed in accordance with subsection 62-762.801(3), F.A.C.

| TABLE AST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Year Tank or |  |  |  |  |
| Integral Piping |  |  |  |  |
| Installed | 1993 | 2000 | 2005 | 2010 |
| +Before July 13, 1998 | P | TVX | W | U |

Key to Table AST

P = With the exception of high viscosity bulk product piping, bulk product piping in contact with soil and not in secondary containment shall be tested in accordance with API RP 1110, ASME B31.4, or an equivalent method approved by the Department in accordance with Rule 62-762.851, F.A.C. Such testing shall be performed annually thereafter.

T =

(1) With the exception of siting and material construction standards, Category-A and Category-B systems shall meet the performance standards of Rule 62-762.501, F.A.C. In addition:

(a) Storage tank system construction standards that include cathodic protection remain applicable; and

(b) Storage tanks where the entire bottom of the tank is in contact with concrete do not have to seal the concrete beneath the tank until such time that the tank bottom is replaced. However, concrete secondary containment systems designed in accordance with sub-subparagraph 62-762.501(1)(e)3.a., F.A.C., do not have to be sealed.

(2) Category-A bulk product piping in contact with the soil shall be upgraded with secondary containment, unless:

(a) A structural evaluation is performed in accordance with API 570, as specified in “U” (2)(b), of Table AST, and results of the structural evaluation indicate that the bulk product piping has remaining useful life; or

(b) The integral piping conveys high viscosity regulated substances, that are exempt from secondary containment in accordance with subparagraph 62-762.501(3)(e)4., F.A.C.; or

(c) The integral piping is protected from corrosion and is tested annually in accordance with ASME B31.4, API 1110, or an equivalent method approved by the Department in accordance with Rule 62-762.851, F.A.C. This piping shall have secondary containment by January 1, 2010, in accordance with “U” of Table AST.

(3) Initial internal and external inspections, examinations, and tests for each tank shall be performed in accordance with API Standard 653, and an appropriate reinspection interval for each tank shall be established in accordance with API Standard 653. If any deficiency is discovered during the inspections, the person performing the evaluation of the tank in accordance with API 653 must verify that the tank is ready for service before the storage tank is put back into service. This verification must be documented in the internal inspection records. Future tests for each tank shall be performed in accordance with the inspection interval established in accordance with API 653 (1996). Baseline inspections already conducted according to the API Standard 653 (1991) will be accepted.

(4) As an alternative to installing secondary containment underneath an AST Category-A or Category-B storage tank, the interior bottom of the tank and at least 18 inches up the sides may be internally lined in accordance with API RP 652. Secondary containment must nonetheless be installed in the dike field area and be continuously bonded to the perimeter of the tank foundation.

U =

(1) All internally lined single bottom storage tanks, with the exception of tanks exempt under paragraph 62-762.501(4)(a), F.A.C., shall be upgraded with secondary containment.

(2) All AST Category-A bulk product piping in contact with the soil, except for piping exempt from secondary containment requirements under subparagraph 62-762.501(8)(e)4., F.A.C., shall be:

(a) Upgraded with secondary containment in accordance with paragraph 62-762.501(1)(e), F.A.C.; or

(b) Instead of being upgraded with secondary containment, be evaluated for structural integrity by:

1. Establishing and maintaining the piping inspection intervals in accordance with API 570, Section 4-2, by January 1, 2000;

2. Determining the remaining life of the system in accordance with API 570, Section 5.0, by January 1, 2000. If the determination indicates that the piping:

a. Must be repaired, then the piping shall be repaired within three months of the determination in accordance with API 570 and Rule 62-762.701, F.A.C.;

b. Is leaking, then the piping must be immediately taken out of operation. If the piping cannot be repaired, it must be closed or upgraded with secondary containment within one year of the determination;

c. Is not leaking, but has corroded to a point where it no longer has structural integrity, then the piping shall be closed, or upgraded with secondary containment by January 1, 2000; or

d. Has remaining useful life, then the piping shall be closed or upgraded with secondary containment when the API 570 inspection and remaining life determination data indicates that closure or replacement is necessary.

3. Providing a certification by a professional engineer registered in the State of Florida that the evaluation meets the above criteria.

V =

(1) Secondary containment for cut and cover or concrete storage tanks.

(2) Spill containment in accordance with paragraph 62-762.501(1)(c), F.A.C.

(3) Dispenser liners for shop-fabricated tanks in accordance with paragraph 62-762.501(2)(e), F.A.C.

(4) Secondary containment in accordance with paragraphs 62-762.501(1)(e) and (2)(c), F.A.C., for dike field areas of facilities with shop-fabricated tanks having dike field area secondary containment that is constructed of concrete or installed with synthetic liners not meeting these requirements.

W =

(1) Secondary containment in accordance with paragraphs 62-762.500(1)(e) and (3)(c), F.A.C., for dike field areas of facilities with field-erected tanks having dike field area secondary containment that is constructed of concrete or installed with synthetic liners not meeting these requirements.

(2) Secondary containment for small diameter piping extending over surface waters.

(3) Secondary containment for small diameter petroleum contact water piping in contact with the soil.

X = Deadline to determine integrity of single wall bulk product piping with an API 570 structural integrity evaluation in accordance with the option for Category-A systems in “U” of Table AST.

Specific Authority 376.303 FS. Law Implemented 376.303 FS. History–New 6-21-04.