Notice of Bid/Request for Proposal

DEPARTMENT OF CHILDREN AND FAMILIES

Northeast Florida State Hospital Fire Alarm Fiber Replacement

GENERAL AND TECHNICAL SPECIFICATIONS

Project No. DCF-21030300

Project Title: Fire Alarm Fiber Replacement

Project Location: NORTHEAST FLORIDA STATE HOSPITAL, STATE ROAD 121, SOUTH MACCLENNY, FLORIDA 32063

STATE OF FLORIDA, FLORIDA DEPARTMENT OF CHILDREN AND FAMILIES, OFFICE OF GENERAL SERVICES, DESIGN & CONSTRUCTION, 1317 WINEWOOD BOULEVARD, BUILDING 3, ROOM 205 F, TALLAHASSEE, FL 32399-0700

ARCHITECT/ENGINEER’s Name: Florida Department of Children and Families, Office of General Services, Street Address: Design & Construction, Jimmie Padgett, 1317 Winewood Boulevard, Building 3, Room 205 F, Tallahassee, Florida 32399-0700, Telephone Number: (850)717-4303

Set No.__________________

Date Issued: November 2, 2020

A-1	INVITATION TO BID

Proposals are requested from QUALIFIED CERTIFIED CONTRACTORS by the State of Florida, Department of Children and Families, hereinafter referred to as OWNER, for the construction of:

PROJECT NO: DCF - 21030300

TITLE: Northeast Florida State Hospital Fire Alarm Fiber Replacement.

SITE:  NORTHEAST FLORIDA STATE HOSPITAL, STATE ROAD 121 SOUTH, MACCLENNY, FLORIDA, 32063

PREQUALIFICATION: Each prime Bidder shall be state-certified in accordance with Chapter 489, Florida Statutes, as a Roofing Contractor.  Bids from firms not able to furnish proof of the required certification are subject to disqualification.

PROPOSAL: Bids must be submitted in full in accordance with the requirements of the Drawings and the General and Technical Specifications, which may be examined and obtained from the ARCHITECT/ENGINEER / Project Manager:

A/E: Department of Children and Families, Office of General Services, Design, and Construction. 1317 Winewood Blvd., Building #3, Room 205-F, Tallahassee, Florida 32399-0700

TEL#: (850)717-4303, E-MAIL: jimmie.padgett@myflfamilies.com

BID DOCUMENTS: Full sets of Drawings and Specifications may be requested from the ARCHITECT/ENGINEER/PROJECT MANAGER by emailing the A/E email listed above.

MANDATORY PRE-BID MEETING: A mandatory pre-bid meeting will be held on Thursday, December 17, 2020 at 10:00 a.m. Eastern time, the meeting will be held at Northeast Florida State Hospital Maintenance Building #19, Conference Room, State Road 121 South, MacClenny, Florida 32063.

BONDING REQUIREMENTS: See Section B-11 for bid guarantee requirements.  See Section C-5 for Public Construction bond requirements.

BID OPENING: Sealed bids will be received, publicly opened and read aloud at:

DATE AND TIME: Thursday, January 21, 2021, 10:00 a.m. Eastern time

LOCATION: Northeast Florida State Hospital Maintenance Building #19, Conference Room, State Road 121 South, MacClenny, Florida 32063.

SECTION 01010

SUMMARY OF WORK

STATE PROJECT NO.: DCF – 21030300

PART 1 – GENERAL

1.1 SUMMARY

The project overall scope of work is to replace the facility overhead multi-mode fiber with underground single-mode fiber at Northeast Florida State Hospital (NEFSH).

Scope of work required: Install new 6-strand single-mode fiber to 50 buildings in existing underground conduit, where available.

A. The Florida Department of Children and Families (DCF) (Owners), Office of General Services, in conjunction with Northeast Florida State Hospital Maintenance will provide construction administration for this project.

B. All work will be completed at the Northeast Florida State Hospital located at, 7487 South State Road 121, Macclenny, Florida, 32211

Instructions to bidders.

1. Prospective bidders can request a copy of the bid documents by emailing Jimmie.Padgett@myflfamilies.com.

2. The bid must be submitted in triplicate in a sealed envelope, clearly marked on its face "SEALED BID PROJECT NO. DCF- 21030300, NEFSH Fire Alarm Fiber Replacement.”

3.  The Exhibits that must be completed are # 1, 2, 4, 6, 7 & 8.  If a bidder does not complete these exhibits, then the bid will be considered non-responsive and not accepted. Exhibits # 9 and # 10 are not required. Exhibit # 3 is the contract.  Exhibit # 11 - # 13 will be used after the contract is awarded.

4. All communication must be in writing to the contact person listed in the Invitation to Bid.

Project scope of work:

1.       Install a 6-strand of G.625.D single-mode fiber to 50 buildings to be used for fire alarm control panels.

2.       All installed fiber will need to be tested and the results from each strand should be provided to the customer in both a printed binder and a PDF file.

3.       A fiber termination can (fiber termination box) will need to be provided and installed near the fire panel.  To protect the fiber, metal conduit will need to be provided both between the in-ceiling innerduct and the can and between the can and the fire panel.

4.       All fiber terminations will be clearly labeled to include the building that it terminates in and a numerical fiber designation (e.g. 07-01 through 07-06, 32-01 through 32-06, etc.)

5.       All pigtails and fusion splicing will be included in the bid.

6.       After the mandatory pre-bid meeting, each contractor must look at each building location before bidding the project.

7.       Fiber will enter the building in the existing conduit and terminate into the existing IDF for that building.  Once terminated, innerduct conduit should be used between the IDF and the fire alarm termination location in each building.

8.       There should be a service loop at the MDF, the IDF, and inside the fiber can at the fire alarm panel.  The can loop should be at least 24 inches long.

9.       Site coordination must be planned in advance with local Maintenance or Information Technology staff.

10.   Any installed handholds, pull boxes, or service loops must meet BICSI standards.

11.   Any splicing performed outside of the IDF or MDF must be fusion-spliced and protected from the elements per industry standards.

12.   Where new conduit is needed, it must be at least 2 inches in inside diameter, be installed underground at 36 inches with a copper trace line, have a spare pull line installed, and not exceed 60% fill.  Contractor verifies.

13.   There are two buildings without existing underground conduit to build # 27 and # 119.  These buildings will require new underground conduit.

14.   At any point where installing new fiber would fill the conduit beyond 75% fill, new conduit must be installed.

15.   All single-mode fiber should be terminated using MT-RJ connections at both the MDF and the IDF.

16.   All MDF, IDF, and fire panel terminations will need to be placed in a vendor-supplied termination canister utilizing the highest density possible to consume the least amount of rack or wall space and still allow for the required service loops.

17.   All fiber will terminate in building 3.  Building site plans and current underground fiber conduit locations will be given out at the mandatory pre-bid meeting.

18.   Three 1-meter MT-RJ to MT-RJ single-mode fiber optic patch cables should be provided for every IDF termination location and three 1-meter MT-RJ to ST single-mode fiber optic patch cables should be provided for every fire panel termination location.

19.   All work must be completed within 100 days of the notice to proceed.

20.   An as-built drawing of both internal and external fiber locations will need to be provided at the end of the project.

21.   The successful vendors will be responsible for performing, scheduling, and requesting all required permits and licenses at no expense to the Department.

22.   Contractor is responsible for their own locate services.  Free locate will not perform services on State property.

23.   Each bidder must have five years of experience installing fiber-optic cabling.

24.   If, during the installation of new cabling, there are any damages to the existing fiber-optic infrastructure, the vendor must be prepared to immediately perform repairs.

25.   Each day, all contractors will need to provide negative COVID-19 tests within a rolling 14 days during the period that they work at the facility.  Daily screenings, including temperature testing, will be performed each time a contractor comes onto the facility.

26.   Additional maps and documents will be provided at the Mandatory bid conference.

27.   Put in a $ 20,000.00 dollar budget number to repair / replace or address and unforeseen issues that were not accounted for or know at this time.  After the unforeseen issue is discovered, DCF will request a detailed cost quote to repair or replace the additional work (including OH&P). DCF will review the detailed proposal with the cost break down to determine if the quote is acceptable. If the additional work is needed and DCF and the contractor cannot agree on the cost, then DCF will direct the contractor to do the work on time and material. This time and material will be signed off buy a NEFSH facility maintenance staff member for verification. If the money is not allocated for any work, then the $ 20,000 dollars or portion of the $ 20,000 that is not spent will not be billed in the contract.  Show the $ 20,000 dollars in schedule of values.

28.   January 7, 2021, 12:00 Noon Eastern Time will be the cut off for question and answers.

29.   Provide an alternate price to remove the old overhead fiber after the job has been completed. This could be up to a year after the project is completed that the facility would be ready for the fiber to be removed.