- 64E-5.1408 Fire Protection.

(1) The radiation room at a panoramic irradiator must have heat and smoke detectors. The detectors must activate an audible alarm. The alarm must be capable of alerting a person who is prepared to summon assistance promptly. The sources must become fully shielded automatically and the air handling systems within the radiation room must be disabled automatically if a fire is detected.

(2) The radiation room at a panoramic irradiator must be equipped with a fire suppression or extinguishing system capable of extinguishing a fire without the entry of personnel into the room. The system for the radiation room must have a shut-off valve to control flooding into unrestricted areas.

Rulemaking Authority 404.051(4) FS. Law Implemented 404.051(1), (5), (6), 404.061, 404.081, 404.141 FS. History–New 8-14-96, Formerly 10D-91.1508.