Notice of Variances and Waivers

DEPARTMENT OF BUSINESS AND PROFESSIONAL REGULATION

Division of Hotels and Restaurants

RULE NO.:	RULE TITLE:

61C-5.001	Safety Standards

The Department of Business and Professional Regulation, Division of Hotels and Restaurants, Bureau of Elevator Safety hereby gives notice: On April 1, 2022, the Division issued an order. The Final Order was in response to a Petition for a Variance from Vonderburg Properties Inc., filed March 15, 2022, and advertised on March 21, 2022, in Vol. 48, No. 55, of the Florida Administrative Register. No comments were received in response to the petition. The Final Order on the Petition for Variance denies the Petitioner a variance from Rules 2.7.4, 2.8.5.1, 2.8.5.2, and 2.8.5.3, ASME A17.1, 2013 edition, as adopted by Rule 61C-5.001 Florida Administrative Code that requires a clear headroom of no less than 84 inches in the elevator machine room or below suspended air conditioning equipment, air conditioning equipment to not be located directly above elevator equipment, and the provision of means to collect and drain condensation water from these spaces with such drains not located directly above elevator equipment, because the Petitioner has not demonstrated that the purpose of the underlying statute has been met and that the Petitioner would suffer a substantial hardship if required to comply with this rule (VW2022-024).

A copy of the Order or additional information may be obtained by contacting: Division of Hotels and Restaurants, Bureau of Elevator Safety, 2601 Blair Stone Road, Tallahassee, Florida 32399-1013, dhr.elevators@myfloridalicense.com.