Miscellaneous

DEPARTMENT OF BUSINESS AND PROFESSIONAL REGULATION

Florida Building Commission

RULE NO.:	RULE TITLE:

61G20-1.001	Florida Building Code Adopted

Notice of Florida Building Code Binding Interpretation

NOTICE IS HEREBY GIVEN THAT the Binding Interpretation Panel has issued a binding interpretation pursuant to Section 553.775, Florida Statutes, submitted by John Cramer, and accepted by BOAF on April 21, 2022. The following is a summary of the interpretation:

Appeal question requiring a response: Does NFPA 58, Section 6.3.2.3, as referenced in the Florida Building Code, 6th Edition (2017), require a measurement to the building foundation or to the line of the overhang that could have a future infill?

Answer: The appropriate measurement, in this specific situation, is to the building wall foundation. A proposal to infill or add on to the existing building would be evaluated at the time of a future permit application review.

Comment: The Panel based this answer relating to the measurement of the required distance to place an underground ASME (LP-gas) container form a building on the plain language of the code standard versus measuring to the overhang of a building, which is not the building wall.