- 69A-43.0095 Individually Annunciated at Panel.

Single station smoke detectors which annunciate at a panel at a supervised location, where used, shall meet the following:

(1) All means of interconnecting equipment, devices and/or appliances shall be monitored for the integrity of the conductors or equivalent so that the occurrence of a single open or a single ground trouble condition in the installation conductors and their restoration to normal shall be automatically signaled as “trouble” at the panel in the supervised location.

(2) Trouble signals shall be audible and distinctive from alarm signals, and shall comply with NFPA 72, Section 1-5.4.6, the edition as adopted in rule Chapter 69A-3, F.A.C.

(3) The annunciator system shall have primary power supplied in accordance with NFPA 72, Section 1-5.2.4, the edition as adopted in rule Chapter 69A-3, F.A.C., and secondary power supplied in accordance with NFPA 72, Section 1-5.2.5, the edition as adopted in rule Chapter 69A-3, F.A.C.

Rulemaking Authority 509.215, 633.104, 633.206(1)(b), 721.24(5) FS. Law Implemented 509.215, 633.104(1), 633.206(1)(b), 721.24(5) FS. History–New 5-14-91, Amended 9-6-01, Formerly 4A-43.0095.