Notice of Change/Withdrawal

DEPARTMENT OF ENVIRONMENTAL PROTECTION

RULE NO.:	RULE TITLE:

62-610.573	Storage Requirements

NOTICE OF CORRECTION

Notice is hereby given that the following correction has been made to the proposed rule in Vol. 50 No. 220, November 8, 2024 issue of the Florida Administrative Register.

This corrects coding errors and includes existing rule language.

62-610.573 Storage Requirements.

(1) through (2) No change.

(3) A separate, off-line system shall be provided for storage of off-spec reclaimed reject water not associated with a potable reuse project. Off-spec reclaimed  Reject water storage shall have sufficient capacity to ensure retention of reclaimed water of unacceptable quality. At a minimum, for treatment facilities required to provide full treatment and disinfection, this capacity shall be the volume equal to three days flow at the average daily permitted flow of the treatment plant, or the average daily permitted flow of the reuse system, whichever is less. If full treatment and disinfection is not required, the capacity requirement shall be reduced to one day’s flow. Provisions for recirculating this off-spec reclaimed reject water to other parts of the treatment plant for further treatment shall be incorporated into the design. Off-spec reclaimed water  Reject storage shall not be required if another permitted reuse system requiring lower levels of preapplication treatment or effluent disposal system is capable of discharging the reject water in accordance with the requirements of Chapter 62-620, F.A.C. Off-spec reclaimed water Reject storage ponds shall be lined or sealed to prevent measurable seepage, as described in Rule 62-610.414, F.A.C.

(4) No change.

(5) Off-spec water storage requirements for potable reuse projects are in Chapter 62-565, F.A.C.

Rulemaking Authority 403.051, 403.061, 403.087 FS. Law Implemented 403.021, 403.051, 403.061, 403.062, 403.085, 403.086, 403.087, 403.088 FS. History–New 4-4-89, Amended 4-2-90, Formerly 17-610.573, Amended 1-9-96, 8-8-99, 4-1-21, xx-xx-xx.