- 62-565.540 Monitoring Requirements for Advanced Treatment Water Facilities and Potable Reuse Systems.

(1) For the purposes of this Chapter, all analytes and parameters shall be measured using approved EPA drinking water test methods, as identified in Rule 62-550.550, F.A.C. When an approved EPA drinking water test method is unavailable, other accepted published methods approved by the department shall be used for measuring.

(2) In addition to the surrogate and operational parameters monitoring requirements in paragraphs 62-565.560(7)(c) and (d), and subsections 62-565.560(8) and (9), F.A.C., the minimum requirements for sampling and monitoring are specified in Table 1 below:

Table 1: Monitoring Frequencies for ATWFs

| Constituent or Disinfectant Residual Group | Frequency of Routine Monitoring | Sample Type | Monitoring Location |
| --- | --- | --- | --- |
| Flow | Continuous | In-line meter | ATWF Influent, Internal Outfall, and ATWF Effluent |
| pH | Continuous | In-line meter | ATWF Influent, Internal Outfall, and ATWF Effluent |
| Temperature | Continuous | In-line meter | ATWF Influent, Internal Outfall, and ATWF Effluent |
| CBOD5 | Daily | Grab | ATWF Influent |
| TSS | Daily | Grab | ATWF Influent, Internal Outfall, and ATWF Effluent |
| Total Organic Carbon (TOC) | Daily | Grab | ATWF Influent, Internal Outfall, and ATWF Effluent |
| Total Organic Halogen (TOX) | Weekly | Grab | ATWF Influent, Internal Outfall, and ATWF Effluent |
| Giardia lamblia, Cryptosporidium, and enteric viruses | Monthly | Grab | ATWF Influent and ATWF Effluent |
| Total coliform | Daily | Grab | ATWF Effluent |
| E. coli | Daily | Grab | ATWF Effluent |
| Nitrate and Nitrite | Monthly | Composite | ATWF Effluent |
| Inorganics1 | Monthly | Composite | ATWF Effluent |
| Chlorine and/or Chloramines2 | Continuous | In-line meter | ATWF Effluent |
| Sodium | Monthly | Grab | ATWF Influent, Internal Outfall, and ATWF Effluent |
| Chlorine Dioxide3 | Continuous | In-line meter | ATWF Effluent |
| Chlorite3 | Daily | Grab | ATWF Effluent |
| Bromate4 | Daily | Grab | ATWF Effluent |
| Volatile Organics1 | Monthly | Grab | ATWF Effluent |
| Synthetic Organics1 | Monthly | Composite | ATWF Effluent |
| Secondary Contaminants1 | Monthly | Composite | ATWF Effluent |
| Gross alpha, Radium-226 and Uranium1 | Monthly | Grab | ATWF Effluent |
| Beta Particle and Photon Radioactivity1 | Monthly | Grab | ATWF Effluent |
| Ultraviolet Dose5 | Continuous | In-line meter | Internal Outfall |
| Ultraviolet Transmission at 254 nanometers5 | Continuous | In-line meter | Internal Outfall |
| Ultraviolet Light Intensity5 | Continuous | In-line meter | Internal Outfall |
| Ozone4 | Continuous | In-line meter | ATWF Effluent |
| Perfluorooctanoic Acid (PFOA)6 | Quarterly | Grab | ATWF Influent and ATWF Effluent |
| Perfluorooctane Sulfonic Acid (PFOS)6 | Quarterly | Grab | ATWF Influent and ATWF Effluent |
| Perfluorohexane Sulfonate (PFHxS)6 | Quarterly | Grab | ATWF Influent and ATWF Effluent |
| Perfluorononanoic Acid (PFNA)6 | Quarterly | Grab | ATWF Influent and ATWF Effluent |
| Hexafluoropropylene Oxide Dimer Acid (HFPO-DA)6 | Quarterly | Grab | ATWF Influent and ATWF Effluent |
| Perfluorobutane Sulfonate (PFBS)6 | Quarterly | Grab | ATWF Influent and ATWF Effluent |
| Hazard Index6, 7 | Quarterly | Calculated | ATWF Influent and ATWF Effluent |

1Inorganics, Volatile Organics, Synthetic Organics, Secondary Contaminants, Gross alpha, Radium-226 and Uranium, and Beta Particle and Photon Radioactivity shall be as defined in Chapter 62-550, F.A.C.

2For those systems using chlorine or chloramines for disinfection.

3For those systems using chlorine dioxide for disinfection.

4For those systems using ozone for disinfection.

5For those systems using ultraviolet for disinfection.

6Per- and Polyfluoroalkyl Substances (PFAS) field testing, sample collection and preservation, laboratory testing, including quality control procedures, and all record keeping shall comply with Chapters 62-160 and 62-550, F.A.C. The analytical test methods shall be sufficiently sensitive to ensure department-established MDLs and PQLs are met.

7The Hazard Index (HI) is made up of a sum of fractions. Each fraction compares the level of each PFAS measured in the water to the highest level determined not to have risk of health effects.

Step 1. Divide the measured concentration of PFHxS by the health-based value of 9 ng/L.

Step 2. Divide the measured concentration of PFNA by the health-based value of 10 ng/L.

Step 3. Divide the measured concentration of HFPO-DA by the health-based value of 10 ng/L.

Step 4. Divide the measured concentration of PFBS by the health- based value of 2000 ng/L.

Step 5. Add the ratios from steps 1-4 together using the following equation:

Hazard Index = ([PFHxS]/[10 ng/L]) + ([PFNA]/[10 ng/L]) + ([HFPO-DA]/[10 ng/L]) + ([PFBS] /[2000 ng/L])

Step 6. To determine HI compliance, repeat steps 1-5 for each sample collected in the past year and calculate the average HI for all the samples taken in the past year.

(3) ATWFs discharging to surface waters of the state shall also be subject to the applicable monitoring requirements established in Chapters 62-302, and 62-304, F.A.C.

(4) For Giardia lamblia, Cryptosporidium, and enteric viruses, if there are no detects in the advanced treated water for two years, the permittee may notify the Department of the applicant’s intent to transition to bi-annual monitoring.

(5) With the exception of radionuclides, for the parameters listed in Table 1 which have an established MCL, if there are no exceedances of one half of the established MCL in finished advanced treated water samples for one year, the permittee may notify the Department of the applicant’s intent to transition to quarterly sampling.

(6) With the exception of radionuclides, for the parameters listed in Table 1 which have an established MCL, if there are no exceedances of one half of the established MCL in finished advanced treated water samples for two years following the transition to quarterly sampling, the permittee may notify the Department of the applicant’s intent to transition to bi-annual sampling.

(7) For the radionuclides identified in Table 1, if there are no exceedances of one half of the established MCL in finished advanced treated water samples for one year, the permittee may notify the Department of the applicant’s intent to transition to quarterly sampling.

(8) For the radionuclides identified in Table 1, if there are no exceedances of one half of the established MCL in finished advanced treated water samples for one year following the transition to quarterly sampling, the permittee may notify the Department of the applicant’s intent to transition to annual sampling.

(9) For the PFAS and HI identified in Table 1, if there are no exceedances of one half of the established MCL for all PFAS and HI constituents in finished advanced treated water samples for one year, the permittee may notify the Department of the applicant’s intent to transition to triennial sampling.

(10) For the PFAS and HI identified in Table 1, if there are no exceedances of the MCL for all PFAS and HI constituents in finished advanced treated water samples for one year, the permittee may notify the Department of the applicant’s intent to transition to annual sampling.

(11) If a permittee is on reduced monitoring for any of the parameters identified in subsections 62-565.540(4)-(10), F.A.C., and does not meet the reduced monitoring criteria for any sampling event, the permittee shall resume monitoring in accordance with the frequencies outlined in Table 1 for that parameter.

(12) Continuous Monitoring of pH.

(a) The permittee shall maintain the pH of reclaimed water and advanced treated water within the range set forth in the ATWF permit, except excursions from the range are permitted subject to the following limitations:

1. The total time during which the pH values are outside the required range of pH values shall not exceed 7 hours and 26 minutes in any calendar month; and

2. No individual excursion from the range of pH values shall exceed 60 minutes.

(b) The applicant may request an adjustment of the requirements set forth in paragraph (a) of this subsection with respect to the length of individual excursions from the range of pH values, and the Department shall approve the requested adjustment if a different period of time is appropriate based upon the treatment system, plant configuration or other related technical factors.

(c) An excursion is an unintentional and temporary incident in which the pH value of reclaimed water or advanced treated water exceeds the range set forth in the advanced treatment water facility permit.

(13) The Department shall allow use of continuous monitoring equipment, for those parameters identified in Table 1 requiring a grab sample, if all of the following conditions are met:

(a) The applicant provides an affirmative demonstration that the proposed monitoring equipment will provide a means for controlling the process that is at least as reliable and accurate as a grab sample.

(b) The proposed monitoring equipment will generate a continuous reading.

(c) The proposed monitoring equipment will be equipped with an automated data logging or recording device.

(d) The proposed monitoring equipment shall be calibrated according to the requirements of Chapter 62-160, F.A.C.

(e) The proposed monitoring equipment shall be maintained according to the manufacturer’s operation and maintenance instructions.

(f) The use of the proposed monitoring equipment and setpoints associated with use of the proposed monitoring equipment shall be fully incorporated into the operating protocol.

(14) In addition to the monitoring requirements established in subsection 62-565.540(2), F.A.C., ATWFs shall conduct semi-annual sampling of the water entering and exiting the ATWF for the toxic pollutants that have been identified under 40 CFR Part 122, Appendix D, (adopted and incorporated by reference in paragraph 62-620.100(3)(b), F.A.C., effective October 8, 2021).

(15) Monitoring Locations.

(a) All samples shall be collected in accordance with the monitoring locations identified in table 1 above.

(b) For influent sampling, a minimum of one sample shall be taken at every entry point to the treatment system that is representative of each source before treatment. If an ATWF draws water from more than one source and the sources are combined before treatment, samples shall be taken at an entry point to the treatment system during periods of typical operating conditions (e.g., when water is representative of the sources being used).

(c) For effluent sampling, a minimum of one sample shall be taken at every discharge point from the treatment system that is representative of the advanced treated water leaving the ATWF prior to blending with other sources of water. For ATWFs involving high-level disinfection, compliance with the TSS limitations shall be achieved, and sampled for, after filtration and before application of the disinfectant.

(d) For internal outfall sampling, a minimum of one sample shall be taken at the internal outfall or outfalls identified in the Department approved Operating Protocol.

(e) The location of monitoring sites shall meet the requirements set forth in subsection 62-565.500(11), F.A.C.

(f) Sampling shall demonstrate compliance with the TBTRs for emerging constituents , pathogen reduction, and site-specific indicator compound and surrogate parameter requirements set forth in this chapter.

(g) Samples shall be taken at the monitoring sites specified in the permit, unless the permittee receives prior approval from the Department to use an alternate site where a represenatitve sample can be collected.

(16) Grab samples shall be collected during periods of minimal treatment plant pollutant removal efficiencies. The actual time and flow conditions during which such samples are taken shall be recorded.

Rulemaking Authority 403.861(9), 403.064(17) FS. Law Implemented 403.852(12), 403.861(7), 403.853(6), 403.861(17), 403.064(17) FS. History – New 2-26-25.