- 69A-73.004 Protective Systems and Designs.

(1) Effective January 1, 2026, automatic sprinkler systems shall be installed in accordance with NFPA 13 and NFPA 13R, incorporated by reference in Rule 69A-60.005, F.A.C., as applicable, in all new parking structures.

(a) This provision shall not apply to private garages not exceeding 1000 ft2 (92.9 m2) associated with residential buildings.

(b) This provision shall not apply to a free-standing, one-story covered structure that is open on at least two sides that provides shelter and storage for motor vehicles.

(2) Charging Station Installation of EVSE’s, EVPE’s, or WPTE’s shall be prohibited within 15 feet of any fire hydrant or fire department connection.

(3) Direct current (DC) electric vehicle charging stations shall be listed and labeled in accordance with UL 2202, DC Charging Equipment for Electric Vehicles, Edition 3 (2022), which is hereby incorporated by reference.

(4) Electric vehicle supply equipment shall be listed and labeled in accordance with UL 2594, Electric Vehicle Supply Equipment, Edition 3 (2022), which is hereby incorporated by reference.

(5) Wireless power transfer equipment for transferring power to an electric vehicle shall be listed and labeled in accordance with UL 2750, Wireless Power Transfer Equipment for Electric Vehicles, Edition 1 (2023), which is hereby incorporated by reference.

(6) Electric vehicle power export equipment shall be listed and labeled in accordance with UL 9741, Electric Vehicle Power Export Equipment (EVPE), Edition 1 (2023), which is hereby incorporated by reference.

(7) The materials incorporated by reference in this rule are copyrighted materials that cannot be copied but may be purchased from UL Standards and Engagement at Comm 2000, 151 Eastern Avenue, Bensenville, IL 60106; Phone: 1(888)853-3503; Website: https://www.shopulstandards.com/HowToOrder.aspx. The copyrighted materials may be accessed in a read-only, non-printable, non-downloadable format at the UL Standards website at: https://www.ul.com/news/qa-complimentary-online-access-ul-standards; or may be viewed, during regular business hours, at the offices of:

(a) The Division of State Fire Marshal, 325 John Knox Road, Third Floor, Atrium Building, Tallahassee, Florida 32303; or

(b) The Florida Administrative Code and Register, Florida State Capitol, 400 S. Monroe Street, Room 701, Tallahassee, FL 32399.

Rulemaking Authority 633.206 FS. Law Implemented 633.206 FS. History – New 8-24-25.