Notice of Declaratory Statement

DEPARTMENT OF BUSINESS AND PROFESSIONAL REGULATION
Florida Building Commission
RULE NO.:
RULE TITLE:

61G20-1.001
Florida Building Code Adopted

NOTICE IS HEREBY GIVEN that the Florida Building Commission has issued an order disposing of the petition for declaratory statement filed by Initial Engineers, P.A., on September 29, 2025. The following is a summary of the agency's disposition of the petition: 

Petitioner requested an answer to the following question, based upon the project described within its petition: When the smoke detector and the refrigerant leak detector are both activated, should the 606.4 shut down requirement supersede the ASHRAE 15 run requirement? On December 9, 2025, the Commission provided the following answer: In response to Petitioner’s question, the answer is yes. Pursuant to section 102.4.1 of the Florida Building Code, Building, 8th Edition (2023), where conflicts occur between provisions of the Florida Building Code and referenced codes and standards, the provisions of the Florida Building Code shall apply. Therefore, for the project in question, when the smoke detector and the refrigerant leak detector are both activated, the shutdown requirement of section 606.4 of the Florida Building Code, Mechanical, 8th Edition (2023), supersedes that of the ASHRAE 15 run requirement.

A copy of the Order Disposing of the Petition for Declaratory Statement may be obtained by contacting: Agency Clerk’s Office, Department of Business and Professional Regulation, 2601 Blair Stone Road, Tallahassee, Florida 32399, (850)921-0342, AGC.Filing@myfloridalicense.com.
