Notice of Proposed Rule

DEPARTMENT OF HEALTH
RULE NO.:
RULE TITLE: 
64-4.209
MMTC Solvent-Based Extraction

PURPOSE AND EFFECT: Pursuant to Chapter 2025-199, § 15, Laws of Florida, this rulemaking initiates nonemergency rulemaking to replace emergency rule 64ER21-13, adopted by the Department to implement section 381.986, Florida Statutes.

SUMMARY: This rule sets forth requirements applicable to medical marijuana treatment centers (MMTCs) when processing marijuana using hydrocarbon solvents or other solvents or gases exhibiting potential toxicity to humans.

SUMMARY OF STATEMENT OF ESTIMATED REGULATORY COSTS AND LEGISLATIVE RATIFICATION: 
The Agency has determined that this will not have an adverse impact on small business or likely increase directly or indirectly regulatory costs in excess of $200,000 in the aggregate within one year after the implementation of the rule. A SERC has not been prepared by the Agency. 
The Agency has determined that the proposed rule is not expected to require legislative ratification based on the statement of estimated regulatory costs or if no SERC is required, the information expressly relied upon and described herein: Pursuant to Ch. 2025-199, § 15, Laws of Florida, rules adopted to replace emergency rules are exempt from ss. 120.54(3)(b) and 120.541, F.S.

Any person who wishes to provide information regarding a statement of estimated regulatory costs, or provide a proposal for a lower cost regulatory alternative must do so in writing within 21 days of this notice.

RULEMAKING AUTHORITY: Art. X, § 29, Fla. Const., 

HYPERLINK "https://flrules.org/gateway/cfr.asp?id=%20381.986(8)(e)11.b.,%20381.986(8)(k),%20FS" \t "cfr"
381.986(8)(e)11.b., 381.986(8)(k), FS
LAW IMPLEMENTED: Art. X, § 29, Fla. Const., 

HYPERLINK "https://flrules.org/gateway/cfr.asp?id=%20381.986(8)(e)11.b.,%20FS" \t "cfr"
381.986(8)(e)11.b., FS
A HEARING WILL BE HELD AT THE DATE, TIME AND PLACE SHOWN BELOW: 
DATE AND TIME: June 24, 2026, 9:00 a.m. - 11:00 a.m., unless concluded earlier.

PLACE: Betty Easley Conference Center, 4075 Esplanade Way #182, Tallahassee, FL 32399.

Pursuant to the provisions of the Americans with Disabilities Act, any person requiring special accommodations to participate in this workshop/meeting is asked to advise the agency at least 7 days before the workshop/meeting by contacting: Meredith Hayes OMMURules@FLHealth.gov or at (850)245-4657. If you are hearing or speech impaired, please contact the agency using the Florida Relay Service, 1(800)955-8771 (TDD) or 1(800)955-8770 (Voice).

THE PERSON TO BE CONTACTED REGARDING THE PROPOSED RULE IS: Meredith Hayes OMMURules@FLHealth.gov or at (850)245-4657.

THE FULL TEXT OF THE PROPOSED RULE IS:
64-4.209 MMTC Solvent-Based Extraction. 
(1) For the purposes of this rule, the terms below shall have the following meanings:
(a) “Carbon Dioxide Solvent” means carbon dioxide in a liquid or supercritical state.
(b) “Closed Loop System” means a commercially manufactured extraction system that is sealed during operation and designed to recover all Solvents used during the extraction process through a feedback loop. 
(c) “Extraction Area” means the area of an MMTC’s processing facility that is designed for Solvent-Based Extraction, which the department has inspected and approved for the area’s designated use. 
(d) “Hydrocarbon Solvent” means N-butane, isobutane, propane, pentane, heptane, or any isomer or combination thereof. 
(e) “Independent Engineer” means an engineer, licensed pursuant to Chapter 471, F.S., that is not an employee, owner, officer, board member, or manager of an MMTC.
(f) “Organic Solvent” means a carbon-based substance, that is liquid at room temperature, and is identified as a Class 3 Solvent by the International Council for Harmonisation of Technical Requirements for Pharmaceuticals for Human Use, “ICH Harmonised Guideline, Impurities: Guidelines for Residual Solvents Q3C(R6)” (10/20/2016) incorporated by reference herein and available at https://flrules.org/Gateway/reference.asp?No=Ref-19625. A Hydrocarbon Solvent, which is also classified as a Class 3 Solvent, is considered a Hydrocarbon Solvent and not an Organic Solvent if it is used under a pressure greater than 15 pounds per square inch (psi).
(g) “Plant Material” means leaves, stalks, stems, roots, and any other part of the marijuana plant. 
(h) “Pressure Vessel” means a component of a Closed Loop System containing marijuana Plant Material and Solvents used during Solvent-Based Extraction and designed to withstand pressure greater than 15 psi.
(i) “Solvent” means a Hydrocarbon Solvent, Carbon Dioxide Solvent, or Organic Solvent, as defined in this rule, which is used to dissolve or disperse chemical compounds from marijuana Plant Material in a Closed Loop System 
(j) “Solvent-Based Extraction” means the process of dissolving or dispersing specific chemical compounds from the marijuana Plant Material using a Solvent in a Closed Loop System.
(2) MMTCs may not engage in Solvent-Based Extraction, except as specifically provided for in this rule.
(3) Prior to engaging in Solvent-Based Extraction, an MMTC must submit the following to the department:
(a) A completed Form DH8026-OMMU-05/2026, “Request for Solvent-Based Extraction,” effective 05/26, which is incorporated by reference and available at https://flrules.org/Gateway/reference.asp?No=Ref-19626, or the information required by the Request for Solvent-Based Extraction form through the department’s licensing portal at https://fldohommu.force.com/mmtc;
(b) The certification from an Independent Engineer required by paragraphs (7)(d) and (e) and paragraphs (8)(d) and (e), as applicable;
(c) Evidence that the MMTC has passed the inspection required by subsection (10); 
(d) Standard operating procedures, including employee training plans, as required by subsection (11); and
(e) A floor plan identifying the location of the proposed Extraction Area. 
(4) An MMTC may not engage in Solvent-Based Extraction prior to receipt of written notice of approval from the department that specifies the Solvent(s) the MMTC is authorized to use.
(5) When engaging in Solvent-Based Extraction, an MMTC must only use Solvents that are: 
(a) A minimum purity of 99.5% with a certificate of analysis from the manufacturer to confirm purity;
(b) Free of odorants, bitterants, or other additives; and
(c) Stored, handled, and disposed of in accordance with local, state, and federal regulations. 
(6) An MMTC approved for Solvent-Based Extraction must conduct all Solvent-Based Extraction in the designated Extraction Area of its department-approved processing facility.
(a) Before being used for Solvent-Based Extraction, the designated Extraction Area must pass a Food Safety Good Manufacturing Practices inspection in accordance with s. 381.986(8)(e)9., F.S.
(b) Such Food Safety Good Manufacturing Practices certification must be renewed before expiration of the certification or every two years, whichever occurs first. 
(7) An MMTC approved to conduct Hydrocarbon Solvent-Based Extraction must comply with the following provisions: 
(a) An MMTC must perform Hydrocarbon Solvent-Based Extraction in a Closed Loop System.
(b) Every pressure gauge within the Closed Loop System must have a rating of at least 125% of the maximum operating pressure, as specified in the manufacturer’s maximum operational limits, not to exceed 10,000 psi.
(c) All Pressure Vessels must contain an emergency pressure release system vented to the outside of the facility.
(d) An Independent Engineer must certify that the Closed Loop System was commercially manufactured, is safe for its intended use, and is built to codes of recognized and generally accepted good engineering practices, such as American Society of Mechanical Engineers (ASME); American National Standards Institute (ANSI); Underwriters Laboratories (UL); or the American Society for Testing and Materials (ASTM). 
(e) The certification must include the Independent Engineer’s signature and seal, the serial number of the Closed Loop System being certified, and the name of the MMTC which will use the Closed Loop System. The MMTC must prominently display proof of the certification inside or immediately outside of the Extraction Area. 
(f) All Pressure Vessels must comply with section VIII, Rules for Construction of Pressure Vessels, Division 1 of the ASME Boiler and Pressure Vessel Code (BPVC) (2019 Edition) incorporated by reference herein. The department has determined that posting the incorporated material on the internet would constitute a violation of the federal copyright law. The incorporated materials are available for inspection at the Department of Health, 2585 Merchants Row Boulevard, Tallahassee, Florida 32399-1710, or at the Department of State, R.A. Gray Building, 500 South Bronough Street, Tallahassee, Florida 32399-0250.
(g) All MMTC processing facilities approved for Hydrocarbon Solvent-Based Extraction must comply with National Fire Protection Association (NFPA) 1, Fire Code (2024), Chapter 38.6.2 and NFPA 55 Compressed Gases and Cryogenic Fluids Code (2023), which are both incorporated by reference herein. The department has determined that posting the incorporated material on the internet would constitute a violation of the federal copyright law. The incorporated materials are available for inspection at the Department of Health, 2585 Merchants Row Boulevard, Tallahassee, Florida 32399-1710, or at the Department of State, R.A. Gray Building, 500 South Bronough Street, Tallahassee, Florida 32399-0250. 
(h) The MMTC must prominently display proof of passing the inspection required by subsection (10) inside or immediately outside of the Extraction Area.
(i) The storage, handling, and disposal of Hydrocarbon Solvents must comply with NFPA 55 (2023).
(j) An MMTC may only use Hydrocarbon Solvents, as defined in this rule, for Hydrocarbon Solvent-Based Extraction.
(8) An MMTC approved to conduct Carbon Dioxide Solvent-Based Extraction must comply with the following provisions:
(a) An MMTC must perform Carbon Dioxide Solvent-Based Extraction in a Closed Loop System.
(b) Every pressure gauge within the Closed Loop System must have a rating of at least 125% of the maximum pressure, as specified in the manufacturer’s maximum operational limits, not to exceed 10,000 psi.
(c) All Pressure Vessels must contain an emergency pressure release system vented to the outside of the facility.
(d) An Independent Engineer must perform a field evaluation of extraction equipment, as installed, and certify that all extraction equipment is safe for its intended use and that the Closed Loop System was commercially manufactured, is safe for its intended use, and is built to codes of recognized and generally accepted good engineering practices, such as ASME; ANSI; UL; or ASTM.
(e) The certification must include the Independent Engineer’s signature and seal, the serial number of the Closed Loop System being certified, and the name of the MMTC which will use the Closed Loop System. The MMTC must prominently display proof of the certification inside or immediately outside of the Extraction Area.
(f) All Pressure Vessels must comply with section VIII, Division 1 of the ASME BPVC.
(g) All MMTC processing facilities approved for Carbon Dioxide Solvent-Based Extraction must comply with NFPA 1 (2024), Chapter 38.6.4 , which is incorporated by reference herein. The department has determined that posting the incorporated material on the internet would constitute a violation of the federal copyright law. The incorporated materials are available for inspection at the Department of Health, 2585 Merchants Row Boulevard, Tallahassee, Florida 32399-1710, or at the Department of State, R.A. Gray Building, 500 South Bronough Street, Tallahassee, Florida 32399-0250. 
(h) The MMTC must prominently display proof of passing the inspection required by subsection (10) inside or immediately outside of the Extraction Area.
(i) The storage, handling, and disposal of Carbon Dioxide Solvents must comply with NFPA 55 (2023).
(9) An MMTC approved to conduct Organic Solvent-Based Extraction must comply with the following provisions:
(a) An MMTC must perform Organic Solvent-Based Extraction in a Closed Loop System under a maximum operational pressure of 15 psi.
(b) All MMTC processing facilities approved for Organic Solvent-Based Extraction must comply with NFPA 1 (2024), Chapter 38.6.3 and NFPA 30 Flammable and Combustible Liquids Code (2024), which are both incorporated by reference herein. The department has determined that posting the incorporated material on the internet would constitute a violation of the federal copyright law. The incorporated materials are available for inspection at the Department of Health, 2585 Merchants Row Boulevard, Tallahassee, Florida 32399-1710, or at the Department of State, R.A. Gray Building, 500 South Bronough Street, Tallahassee, Florida 32399-0250. 
(c) The MMTC must prominently display proof of passing the inspection required by subsection (10) inside or immediately outside of the Extraction Area.
(d) The storage, handling, and disposal of any Organic Solvent must comply with NFPA 30 (2024).
(e) An MMTC may only use Organic Solvents, as defined in this rule, for Organic Solvent-Based Extraction.
(10) The MMTC must ensure that the processing facilities and all Solvent-Based Extraction equipment, including the Closed Loop System, are inspected and approved for their use by a local fire code official prior to department approval, and at a minimum biennially thereafter. 
(a) All MMTC processing facilities and all Solvent-Based Extraction equipment must meet any required fire, safety, and building code requirements specified in the Florida Fire Prevention Code (FFPC), NFPA 1 (2024), Chapter 38, and other applicable standards, including any applicable fire, safety, and building codes in the processing, handling, and storage of Solvents.
(b) If the local fire code official declines to perform a fire code inspection, an MMTC may request that a third party, Florida certified fire inspector III perform the required inspection. Such requests must be submitted to the department through the department’s licensing portal at https://fldohommu.my.site.com/mmtc/. 
(11) An MMTC must create, maintain, and comply with written detailed standard operating procedures for the safety and operation of all Solvent-Based Extraction equipment, including the Closed Loop System, within the manufacturer’s equipment safety specifications.
(a) All employees performing any Solvent-Based Extraction must:
1. Obtain training on the MMTC’s standard operating procedures prior to performing Solvent-Based Extractions; and
2. Obtain training in safety and application from the manufacturer of the Closed Loop System. The MMTC must maintain documentation of such manufacturer training for all employees performing any Solvent-Based Extraction.
(b) An MMTC must prominently display a list of the names of all trained and certified employees inside or immediately outside of the Extraction Area.
(12) An MMTC may not alter any Closed Loop System. The equipment manufacturer must perform any alterations to the Closed Loop System.
(a) An Independent Engineer must inspect any alteration and certify that the alterations are built to codes of recognized and generally accepted good engineering practices, such as ASME; ANSI; UL; or ASTM.
(b) The certification must include the Independent Engineer’s signature and seal, the serial number of the Closed Loop System being certified, and the name of the MMTC which will use the Closed Loop System. The MMTC must prominently display proof of the certification inside or immediately outside of the Extraction Area. 
(13) An MMTC whose Food Safety Good Manufacturing Practices certification is set to expire in less than 90 days from the effective date of this rule, or whose certification is greater than two years old, shall have 90 days from the effective date of this rule to come into compliance with the requirements of paragraph (6)(b).
Rulemaking Authority Art. X, Sec. 29, Fla. Const., 381.986(8)(e)11.b., 381.986(8)(k) FS. Law Implemented Art. X, Sec. 29, Fla. Const., 381.986(8)(e)11.b. FS. History –New            .
NAME OF PERSON ORIGINATING PROPOSED RULE: Bobbie Smith, Director, Office of Medical Marijuana Use

NAME OF AGENCY HEAD WHO APPROVED THE PROPOSED RULE: Joseph A. Ladapo, MD, PhD, State Surgeon General

DATE PROPOSED RULE APPROVED BY AGENCY HEAD: May 28, 2026

DATE NOTICE OF PROPOSED RULE DEVELOPMENT PUBLISHED IN FAR: August 29, 2025

