Notice of Variances and Waivers

DEPARTMENT OF BUSINESS AND PROFESSIONAL REGULATION
Division of Hotels and Restaurants

RULE NO: RULE TITLE
61C-5.006: Elevator Fees; Construction and Alteration Permits; Annual Certificates of Operation; Delinquency Fee; Temporary Operation Permits Certificate Replacement

NOTICE IS HEREBY GIVEN that on March 7, 2007, the Division of Hotels and Restaurants, Bureau of Elevator Safety, received a petition for Rule 61C-5.006, F.A.C., Elevator Fees; Construction and Alteration Permits; Annual Certificates of Operation; Delinquency Fee; Temporary Operation Permits Certificate Replacement, an Emergency Variance from ASME A17.1 2005 Edition, Rules 2.26.1.4.4, 2.27.3.1.6(h), 2.27.3.2.5(05a) and 2.27.3.3.1(04) requiring a transfer switch in the machine room rendered inactive by the top-of-car inspection switch, a continuous audible signal when on Phase I, the recall level to remain at the designated level when the car is recalled from the alternate level and a door open and close button be provided on the same panel. The request was submitted by Fidel Mendiguren of Ace Elevator Company on behalf of Florida Ridge Condominiums, Bldgs. 3, 6 and 10.

A copy of the Petition for Variance or Waiver may be obtained by contacting: Mark Boutin, Bureau of Elevator Safety, 1940 North Monroe Street, Tallahassee, Florida 32399-1013. The Bureau of Elevator Safety will accept comments concerning the Petition for 14 days from the date of publication of this notice. To be considered, comments must be received on or before 5:00 p.m.