## 64E-6.009 Alternative Systems.

When approved by the DOH county health department, alternative systems may, at the discretion of the applicant, be utilized in circumstances where standard subsurface systems are not suitable or where alternative systems are more feasible. Unless otherwise noted, all rules pertaining to siting, construction, and maintenance of standard subsurface systems shall apply to alternative systems. In addition, the DOH county health department may, using the criteria in subsection 64E-6.004(4), F.A.C., require the submission of plans prepared by an engineer licensed in the State of Florida, prior to considering the use of any alternative system.

(1) Waterless, incinerating or organic waste composting toilets – may be approved for use if found in compliance with standards for Wastewater Recycle/Reuse and Water Conservation Systems as defined by ANSI/NSF International Standard Number 41, revised May 1983, hereby incorporated by reference, and provided that graywater and any other liquid and solid waste is properly collected and disposed of in accordance with standards established in this chapter. For residences, the required drainfield absorption surface and unobstructed area of the system treating the remaining sewage flow shall be reduced by 25% when waterless, incinerating or organic waste composting toilets are used exclusively for all toilet wastes. Solids removed from waterless, incinerating or organic waste composting toilets shall be mixed with lime, containerized, and disposed of with the solid waste from the establishment. Liquids discharging from waterless, incinerating or organic waste composting toilets shall be plumbed into the onsite system serving the establishment.

(2) Sanitary pit privy – shall not be permitted except at remote locations where electrical service is unavailable. In no case shall such installations be permitted for permanent residences.

(3) Mound systems – are used to overcome certain limiting site conditions such as an elevated seasonal high water table, shallow permeable soil overlying slowly permeable soil and shallow permeable soil located over creviced or porous bedrock. Special installation instructions or design techniques to suit a particular site shall, using the criteria in subsection 64E-6.004(4), F.A.C., be specified on the construction permit in addition to the following general requirements.

(a) Site preparation must render the site in compliance with requirements of subsections 64E-6.006(1)-(6), F.A.C.

(b) Prior to the construction of a mound system, the applicant may fill all or a portion of a lot utilizing slightly limited soil.

(c) The O horizon of original topsoil and vegetation must be removed from beneath the drainfield, shoulder and slope area and the exposed underlying soil plowed or roughened to prevent formation of an impervious barrier between the fill and natural soil. Moderately limited soil material may be used in the construction of mound systems, but shall only be used in the construction of mound slopes and the soil cap. If moderately or severely limited soil is to be replaced beneath the mound, Rule 64E-6.008, F.A.C., Table III, footnote 3. shall be followed.

(d) Where the soil material underlying a mound system is of a similar textural material as that used in system construction, the mound drainfield size shall be based on estimated sewage flows as specified in Rule 64E-6.008, F.A.C., Table I and upon the quality of fill material utilized in the mound system. When estimated sewage flows are calculated to be less than 200 gallons per day, specifications for system design shall be based on a minimum flow of 200 gallons per day. Maximum sewage loading rates for soils used in mound construction shall be in compliance with the following:

| Fill Material | Maximum Sewage Loading Rate to Mound Drain Trench Bottom Surface in gallons per square foot per day | Maximum Sewage Loading Rate to Mound Absorption Bed Bottom Surface in gallons per square foot per day |
| --- | --- | --- |
| Sand; Coarse Sand; and Loamy Coarse Sand | 0.80 | 0.60 |
| Fine Sand Sandy Loam; | 0.80 | 0.60 |
| Coarse Sandy Loam; and Loamy Sand | 0.65 | 0.40 |
| Fine Sandy Loam; Very Fine Sand; Loamy Fine Sand; and Loamy Very Fine Sand | 0.35 | 0.25 |

(e) Where moderately limited soils underlie the mound within 36 inches of the bottom of the drainfield, drainfield sizing shall be based on the most restrictive soil texture existing in the profile to a depth of 36 inches below the bottom of the drainfield, using Table III for soil loading rates.

(f) There shall be a minimum 4 feet separation between the shoulder of the fill and the nearest trench or absorption bed sidewall. Where a portion of the mound slope will be placed adjacent to building foundations, pilings or supports for elevated structures, mobile home walls, swimming pool walls, retaining walls, or similar obstructions there shall be a minimum 5 foot separation between the sidewall of the absorption area and the obstruction. Such obstructions shall impact the slope on no more than 50 percent of the shoulder perimeter. Retaining walls must be designed by a professional engineer licensed in the State of Florida to withstand the lateral earth forces under saturated conditions and to prevent seepage. Where mounds are placed on slopes exceeding 2 percent, the toe of the slope on the downslope side of the mound shall extend an additional 4 inches for each additional 1 percent of slope. To taper the maximum elevation of the mound at the outer perimeter of the shoulder down to the toe of the slope, additional moderately or slightly limited fill shall be placed at a minimum 2 foot horizontal to 1 foot vertical grade where mound height does not exceed 36 inches. Mound heights which exceed 36 inches shall have a slope not steeper than 3 foot horizontal to 1 foot vertical. The entire mound including slopes, shoulders and the soil cap shall be stabilized with vegetation. Slopes steeper than 5:1 shall be sodded or hydroseeded. Soil caps and unsodded slopes must, at a minimum, be hydroseeded or seeded with grass and a layer of hay or similar cover. Where fill material is present in the amount so as to provide a level surface from the top of the required cover over the system over the area where the slopes would normally be located, no slopes shall be required. For example, if the neighboring lot has been permanently filled to the same level as the applicant’s lot, a five-foot separation from the property line to the system will be required, as opposed to requiring the slope area. Stabilization of a mound shall be the responsibility of the septic tank contractor who constructed the mound system unless the written agreement for system construction clearly states the system owner is responsible. Mound slopes which do not conform to permit requirements shall at a minimum be restored to permit specifications prior to stabilizing. Other synthetic or vegetative covers providing protection from mound erosion equal to or better than sod shall be approved by the State Health Office. Final installation approval shall not be granted until sodding, hydroseeding, seeding and haying or other approved stabilization of the mound has occurred. No portion of the drainfield or shoulder area shall be covered with asphalt or a concrete driveway or be subject to vehicular traffic. Landscaping features such as boulders or trees which obstruct drainfield or fill shoulder area shall not be used. Hydroseeding shall be performed in accordance with the product manufacturer’s instructions and Section 7.5, Permanent Seeding, of the Florida Erosion and Sedimentation Control Inspector’s Manual, July 2008, herein incorporated by reference.

(g) There shall be a soil cap of slightly or moderately limited soil material over the drainfield and shoulder area. The soil cap shall be no less than 6 inches thick at the outer perimeter of the shoulder. Additional soil cap material shall be placed over the mound and graded to provide drainage off and away from the mound. The maximum depth from the bottom of the drainfield to the finished ground surface shall not exceed 30 inches after natural settling.

(h) The site shall be landscaped according to permit specifications and shall be protected from automotive traffic or other activity that could damage the system. Swales or other surface drainage structures shall be utilized to prevent water shed from mounds draining onto neighboring property.

(i) All fill material used in the construction of systems shall be free of extraneous non-soil material such as grass, roots and any other debris. Shell fragments less than 2.0 mm in diameter are excluded from the classification of extraneous non-soil materials and are considered to be soil particles. Severely limited soil material shall not be used in system construction. Fill material consisting of mechanically crushed and sieved rock shall not be used in system construction.

(j) Where moderately limited soil is used to construct a mound system, a low pressure distribution network is required.

(4) Filled systems – filled systems shall be constructed in accordance with the minimum requirements for mounds, except as provided for in footnote 5., Table III, and that sewage loading rates to trench or absorption bed bottom areas shall be based on values found in Table III.

(5) Drip irrigation systems – Drip irrigation systems may, at the option of the applicant, be used in lieu of a mineral aggregate drainfield. Drip irrigation systems shall meet all requirements of this chapter except as noted below.

(a) Drip irrigation systems shall receive effluent from an approved aerobic treatment unit or a performance-based treatment system designed to meet at least secondary treatment standards for CBOD5 and TSS, and shall meet the following requirements:

1. Drip irrigation systems shall be designed by an engineer licensed in the State of Florida.

2. The infiltrative area required shall be the same as the area required for a mineral aggregate drainfield with reductions allowed for the reduction of CBOD5 and TSS as noted in this chapter for aerobic treatment units.

3. In an absorption bed configuration, the drainfield area shall be calculated as extending one foot beyond the sides of the outermost emitter lines. Notwithstanding the provision of paragraph 64E-6.014(5)(b), F.A.C., the individual bed size limitation of 1500 square feet does not apply to drip emitter systems.

4. In a trench containing a single emitter line, the drainfield area shall be calculated as 2 feet multiplied by the emitter spacing in feet multiplied by the number of emitters.

5. Drip effluent disposal systems shall be considered pressure distribution systems. Head loss calculations shall be provided to insure proper hydraulic pressure at the emitter. Pump selection shall be indicated in the design specifications. Pump performance curves shall be included in the permit application.

6. Recirculation rates shall be in the design specifications.

7. Check valves, petcocks, inline filters, and vacuum breaking device locations shall be shown on the design drawings.

8. Drip irrigation systems shall be time-dosed over the 24-hour period. Demand control dosing shall override timed-dosing in periods of flow where timed dosing cannot accommodate the excessive flow.

9. Emitter lines shall be designed as a continuous loop circuit with no dead-ends.

10. Emitter lines shall be drawn to scale and emitter spacing shall be indicated on the drawings.

11. Vacuum release valves shall be installed at the highpoint of the emitter lines.

12. The maximum emitter longitudinal spacing on an emitter line shall be 2 feet. The maximum spacing between adjacent emitter lines in an absorption bed configuration shall be 2 feet. The 24-inch separation from the seasonal high water table shall be measured from the emitter orifice. Setbacks shall be measured from the drip emitter lines.

13. The setback from drip emitter lines to building foundations and property lines shall be no less than two feet.

14. The definition of a filled system in Rule 64E-6.002, F.A.C., is not applicable to drip effluent disposal systems. A drip effluent disposal system is considered to be a mound system when any part of the bottom surface of any drip emitter line is located at or above the elevation of undisturbed native soil in the drainfield area. A drip effluent disposal system is considered a standard subsurface drainfield system when the entire bottom surface of every drip emitter line is installed below the elevation of undisturbed native soil in the drainfield area.

15. For mound systems there shall be a minimum 18-inch separation between the shoulder of the fill and the nearest drip emitter line. Mound system slopes shall be in accordance with paragraph 64E-6.009(3)(f), F.A.C., except that a minimum 2 foot separation is required between the nearest drip emitter line and a building foundation, retaining wall, or similar obstruction. Mound systems shall be stabilized in accordance with paragraph 64E-6.009(3)(f), F.A.C.

16. For standard subsurface systems, the elevation of any fill covering the drainfield shall extend no less than 18 inches away from all emitter lines before tapering down to natural grade.

17. Minimum cover on the emitter lines shall be 6 inches for all drip irrigation systems. The maximum cover for all drip irrigation systems shall be no greater than 12 inches.

18. The system shall include a petcock on the dosing pump discharge line for effluent sampling.

19. All systems shall incorporate an automatic mechanism for backwashing or flushing the drip lines and filters.

20. All onsite sewage treatment and disposal systems that include a drip effluent disposal system and aerobic treatment unit shall have a biennial operating permit, a maintenance contract with an approved aerobic treatment system maintenance entity, and shall be inspected in accordance with the requirements of this chapter.

21. Drip irrigation systems shall be designed to have a minimum operating pressure at the emitter head of 10 PSI, a maximum operating pressure at the emitter head of 45 PSI, a maximum system operating pressure of 60 PSI, and a maximum discharge rate per emitter of 1.5 gallons per hour.

22. The hydraulic surge storage requirement of Rule 64E-6.028, F.A.C., does not apply to drip irrigation systems.

23. Drip irrigation systems shall only use components approved by the Bureau of Onsite Sewage Programs.

24. Unobstructed area for drip irrigation systems may be located anywhere on the establishment property that meets the setbacks for unobstructed area and can be accessed via transmission lines, supply lines and return lines installed in accordance with this chapter. The land containing only transmission lines, supply lines and return lines shall not be included in the calculation of unobstructed area.

25. Supply lines and return lines shall be considered as transmission lines for determining setbacks not specified in this section.

26. Except for slopes required to meet the stabilization requirements of paragraph 64E-6.009(3)(f), F.A.C., the area over the drip irrigation drainfield shall be vegetated with plant species specified by the design engineer. The species specified shall not include trees.

(b) Drip irrigation systems shall be monitored during required maintenance visits by visual inspection of the ground surface above the emitter lines for evidence of soil saturation at the ground surface.

(6) Tire chip aggregate systems – tire chip aggregate may be used as a substitute for mineral aggregate in onsite sewage treatment and disposal system drainfields under the following conditions:

(a) The tire chips meet the specifications for mineral aggregate found in this chapter: Mixed tire and mineral aggregate shall be approved where each type of aggregate meets its respective standard and the combined mixture meets the gradation requirements in paragraph 64E-6.014(5)(c), F.A.C.

(b) Exposed wire protrudes no more than one-half (1/2) inch from 90% of the chips.

(c) At least 80% of the bead wire has been removed from the tires to be chipped.

(d) The system receives domestic wastewater only.

(e) Tire chip aggregate shall not be used where the seasonal high water table is less than 12 inches below the bottom of the drainfield at the wettest season of the year.

(f) In all other respects tire chip aggregates and mixed tire-mineral aggregates shall be installed with identical site restrictions and construction requirements as approved mineral aggregates.

(7) Alternative system component and design approval – After innovative system testing is completed, requests for approval of system components and designs which are not specifically addressed in this chapter shall be submitted to the department’s Bureau of Onsite Sewage Programs.

(a) Requests for alternative system component material and design approval shall include:

1. Detailed system design and construction plans by an engineer licensed in the State of Florida,

2. Certification of the performance capabilities of the product submitted by an engineer licensed in the State of Florida,

3. Research supporting the proposed system materials,

4. Empirical data showing results of innovative system testing in the State of Florida; and,

5. A design, installation and maintenance manual showing how to design and install the system in accordance with this chapter for standard, filled, mounded, gravity-fed, dosed, bed and trench configurations.

(b) In addition to those items listed in paragraph 64E-6.009(7)(a), F.A.C., manufacturers of drip effluent disposal system distribution lines, emitters, and components shall apply for and obtain approval from the Bureau of Onsite Sewage Programs for specific model numbers or part numbers prior to inclusion of the components on any site specific permit application. Manufacturer’s of drip effluent disposal system components shall provide design and installation manuals for engineering and construction guidance. Design manuals shall include tables that detail flow rates vs. pressure and pressure loss per length(s) of distribution pipe.

(c) The detailed plans and information submitted with the approval request shall be reviewed by the department onsite sewage program to determine whether or not there is a reasonable certainty of the effectiveness and reliability of the proposed alternative system component. If the department is not satisfied that the information provided provides reasonable evidence of the effectiveness and reliability of the alternative system component and designs, the department shall deny the approval. Department approval of any alternative system component does not guarantee or imply that any individual system installation will perform satisfactorily for a specific period of time. Upon department approval of the material and design, the manufacturer shall list the department approval date in the installation and design manual. Proposals to amend the approved installation and design manual shall be submitted to the bureau for approval. The date of amendment approval shall be included in the manual.

(d) Except as provided for in Part IV of this chapter, alternative drainfield materials and designs shall not be approved which would result in a reduction in drainfield size using the mineral aggregate drainfield system as described in Rule 64E-6.014, F.A.C., and the total surface area of soil at the bottom of the drainfield as the criteria for drainfield sizing comparisons. Alternative system component and design approvals shall not be granted for the following items:

1. Those which, in whole or in part, are used to achieve a more advanced level of treatment than the baseline treatment level specified in part IV of this chapter,

2. Aerobic treatment units,

3. Septic tank designs, filters, seals, and sealants,

4. Additives,

5. Header and drainfield pipe, including their layout; and,

6. Water table separation and setback requirements.

(e) Unless determined unnecessary or impractical by the Department at the time of component approval, effective January 1, 2010, all components shall be labeled with the name of the manufacturer and the model identification of the component. The design, installation and maintenance manual shall show the location of the label and shall include an illustration of a typical label. The label shall be in a location where it will be visible or easily exposed at the time of system inspection. All identifying marks shall be inscribed or affixed at the point of manufacture.

(8) Other alternative systems – systems such as low pressure distribution networks, small diameter gravity sewers, low pressure sewer systems, alternating absorption fields, and sand filters designed and submitted by an engineer who is licensed in the State of Florida, meeting the general requirements of this chapter, shall be approved by the DOH county health department where evidence exists that use of such systems will not create sanitary nuisance conditions, health hazards or pollute receiving waters. Use of an alternative system may require the establishment of procedures for routine maintenance, operational surveillance, and environmental monitoring to assure the system continues to function properly.

(9) Use of a system to serve more than one residence or commercial building under separate ownership and when located on separate lots shall require the establishment of a local sewer district, maintenance franchise, or other legally binding arrangement for the operation and maintenance of such system.

(10) All materials incorporated herein may be obtained from the Bureau of Onsite Sewage Programs at www.MyFloridaEH.com or 4052 Bald Cypress Way, Bin A08, Tallahassee, Florida 32399-1713.

Rulemaking Authority 381.0065(3)(a) FS. Law Implemented 381.0065 FS. History–New 12-22-82, Amended 2-5-85, Formerly 10D-6.49, Amended 3-17-92, 1-3-95, Formerly 10D-6.049, Amended 11-19-97, 2-3-98, 3-22-00, 4-21-02, 6-18-03, 11-26-06, 6-25-09.