Notice of Proposed Rule

DEPARTMENT OF FINANCIAL SERVICES
Division of State Fire Marshal

RULE NO: RULE TITLE
69A-3.012: Standards of the National Fire Protection Association and Other Standards Adopted
PURPOSE AND EFFECT: To require the owner of any commercial, industrial or multiunit residential structure of three units or more constructed of light-frame trusses, to install a symbol approved by the State Fire Marshal on a location near the main entry of the structure.
SUMMARY: The rule provides the size shape color and location of the symbol required on structures constructed of light-frame trusses.
SUMMARY OF STATEMENT OF ESTIMATED REGULATORY COSTS: The agency has determined that this rule will not have an impact on small business. A SERC has not been prepared by the agency.
Any person who wishes to provide information regarding a statement of estimated regulatory costs, or provide a proposal for a lower cost regulatory alternative must do so in writing within 21 days of this notice.
SPECIFIC AUTHORITY: 633.01(1), 633.022, 633.0215, 633.027 FS.
LAW IMPLEMENTED: 633.01, 633.022, 633.0215, 633.027 FS.
IF REQUESTED WITHIN 21 DAYS OF THE DATE OF THIS NOTICE, A HEARING WILL BE HELD AT THE DATE, TIME AND PLACE SHOWN BELOW(IF NOT REQUESTED, THIS HEARING WILL NOT BE HELD):
DATE AND TIME: Friday, August 14, 2009, 10:00 a.m.
PLACE: The conference room at the Atrium Building, 325 John Knox Road, Tallahassee, Florida
THE PERSON TO BE CONTACTED REGARDING THE PROPOSED RULE IS: Jim Goodloe, Chief, Bureau of Fire Prevention, Division of State Fire Marshal, Department of Financial Services, Tallahassee, Florida 32399-0329, phone (850)413-3620

THE FULL TEXT OF THE PROPOSED RULE IS:

69A-3.012 Standards of the National Fire Protection Association and Other Standards Adopted.

(1) through (5) No change.

(6) Notice required for structures with light-frame truss-type construction.

Purpose: The purpose of this rule is to require the placement of an identifying symbol on structures constructed with a light-frame weight truss component in a manner sufficient to warn persons conducting fire control and other emergency operations of the existence of light-frame truss-type construction in the structure.

(a) Definitions.

1. “Light-frame truss-type construction” means a type of construction whose primary structural elements are formed by a system of repetitive wood or light gauge steel framing members.

2. “Approved symbol” means a Maltese Cross measuring 8 inches horizontally and 8 inches vertically, of a bright red reflective color, designed in accordance with Figure 1.

3. “Townhouse” means a single-family dwelling unit constructed in a group of three or more attached units with property lines separating each unit in which each unit extends from foundation to roof with open space on at least two sides.

(b) Any commercial, industrial, or any multiunit residential structure of three units or more (excluding townhouses), which uses horizontal or vertical light-frame truss-type construction in any portion shall be marked with an approved symbol. Each approved symbol shall include within the center circle one of the following designations:

1. Structures with light-frame truss roofs shall be marked with the letter “R”.

2. Structures with light-frame truss floor systems shall be marked with the letter “F”.

3. Structures with light-frame truss floor and roof systems shall be marked with the letters “R/F”.

(c) The approved symbol shall be placed within 24 inches to the left of the main entry door and:

1. Be permanently attached to the face of the structure on a contrasting background, or

2. Be mounted on a contrasting base material which is then permanently attached to the face of the structure.

(d) The distance above the grade, walking surface or the finished floor to the bottom of the symbol shall be not less than 4 feet (48 in).

(e) The distance above the grade, walking surface or the finished floor to the top of the symbol shall be not more than 6 feet (72 in).

(7) In single tenant structures with multiple main entry doors, such as big box retail stores, department stores and grocery stores, the authority having jurisdiction is authorized to require that other main entry doors of the structure be marked with an approved symbol to carry out the purpose in subsection (6) above.

(8) In multiple tenant structures and covered malls with multiple main entry doors, the authority having jurisdiction is authorized to require that other main entry doors be marked with an approved symbol to carry out the purpose in subsection (6) above. In such structures, approved symbols shall be marked on one side only and spaced not closer than 100 feet or at each end of the structure when such structure is less than 100 feet in length.

(9) The owner of each new structure required to comply with this section shall mark the structure with the approved symbol prior to receiving a certificate of occupancy.

(10) The owner of each existing structure required to comply with this section shall mark the structure with the approved symbol within 90 days of the effective date of this rule section.

(11) Where the owner of the structure and the authority having jurisdiction disagree as to the use of light-frame truss-type construction within the structure, the owner shall be granted not more than 45 days to provide written verification from a licensed engineer or licensed architect; otherwise the owner shall comply with the rule.

Figure 1:

Approved Symbol

Light-frame “Roof” only

Light- frame “Floor” only

Light- frame “Floor & Roof”

Rulemaking Specific Authority 633.01(1), 633.022, 633.0215, 633.027 FS. Law Implemented 633.01, 633.022, 633.0215, 633.027 FS. History–New 5-14-86, Amended 2-12-87, 4-8-90, 10-30-91, 4-3-95, 11-27-01, Formerly 4A-3.012, Amended 8-7-05, 5-18-08,__________ .

NAME OF PERSON ORIGINATING PROPOSED RULE: Jim Goodloe, Chief, Bureau of Fire Prevention

NAME OF AGENCY HEAD WHO APPROVED THE PROPOSED RULE: Alex Sink, Chief Financial Officer

DATES PROPOSED RULE APPROVED BY AGENCY HEAD: September 15, 2008 and June 19, 2009

DATE NOTICE OF PROPOSED RULE DEVELOPMENT PUBLISHED IN FAW: February 20, 2009