- 62-532.900 Forms.

The forms used by the Department for permitting and construction of a well are listed below by form number and name. Each form has been incorporated into this rule by reference. Copies of these forms may be obtained by writing to the Department of Environmental Protection, Ground Water Regulatory Section, M.S. 3580, 2600 Blair Stone Road, Tallahassee, Florida 32399-2400. These forms also are available at the five regional water management district offices.

(1) State of Florida Permit Application to Construct, Repair, or Abandon a Well, Form Number 62-532.900(1), incorporated in subsection 62-532.400(1), F.A.C., effective 10-7-10.

(2) State of Florida Well Completion Report, Form Number 62-532.900(2), incorporated in Rule 62-532.410, F.A.C., effective 10-7-10.

TABLE 1

WELL SETBACK DISTANCES

October 7, 2010

| Part A Drinking Water Supply Wells Serving Public Water Systems or Bottled Water Plant Wells |  |  |
| --- | --- | --- |
| RULE | INSTALLATION | SETBACK in feet (footnote) |
| Reuse of Reclaimed Water and Land Application 62-610.421(3) | Slow Rate Land Application Restricted Public Access | 500 (a) |
| 62-610.521(2) | Rapid Rate Land Application | 500 (b) |
| 62-610.621(2) | Overland Flow Systems | 500 |
| 62-610.621(4) | Transmission Facilities Conveying Reclaimed Water to Restricted Public Access Slow Rate Land Application Systems, Rapid Rate Land Application System, or Overland Flow Systems | 100 |
| 62-610.471(1) | Public Access, Residential Irrigation, or Edible Crop Slow-rate Land Application Systems | 75 |
| 62-610.471(3) | Transmission Facilities Conveying Reclaimed Water to Public Access, Residential Irrigation, or Edible Crop Slow-rate Land Application Systems | 75 |
| Domestic Wastewater Residuals 62-640.700(4)(b) | Domestic Wastewater Residuals Land Application Areas | 500 |
| Phosphogypsum Management 62-673.340(2)(d) | Phosphogypsum Stack Systems | 500 (c) |
| Storage Tank Systems 62-761.500(1)(a) and 62-762.501(1)(a) | Aboveground or Underground Storage Tanks | 100 |
| Solid Waste Management Facilities 62-701.300(2)(b) | Solid Waste Disposal Facilities | 500 |
| 62-701.300(12)(a) | Yard Trash Disposal, Storage, or Process | 200 |
| 62-701.300(13) | Storage or Treatment of Solid Waste in Tanks | 100 |
| Permitting and Construction of Public Water Systems 62-555.312(1) | Onsite Sewage Treatment and Disposal Systems | 200 (d), 100 (e) |
| Public Water Systems 62-555.312(3) | Sanitary Hazard as defined in Chapter 62-550, F.A.C., for drinking water supply wells serving public water systems | 100 (f), 50 (g) |
| Feedlot and Dairy Wastewater Treatment and Management Requirements 62-670.500(6)(a) | Dairy Farm Waste - Unlined Storage and Treatment, or High Intensity Areas | 300 |
| 62-670.500(6)(b) | Dairy Farm Waste - Land Application | 200 |

| Part B Drinking Water Supply Wells Serving Limited Use Commercial Public Water Systems and Limited Use Community Public Water Systems |  |  |
| --- | --- | --- |
| RULE | INSTALLATION | SETBACK in feet (footnote) |
| Reuse of Reclaimed Water and Land Application 62-610.421(3) | Slow Rate Land Application Restricted Public Access | 500 (a) |
| 62-610.521(2) | Rapid Rate Land Application | 500 (b) |
| 62-610.621(2) | Overland Flow Systems | 100 |
| 62-610.621(4) | Transmission Facilities Conveying Reclaimed Water to Restricted Public Access Slow Rate Land Application Systems, Rapid Rate Land Application System, or Overland Flow Systems | 100 |
| 62-610.471(1) | Public Access, Residential Irrigation, or Edible Crop Slow-rate Land Application Systems | 75 |
| 62-610.471(3) | Transmission Facilities Conveying Reclaimed Water to Public Access, Residential Irrigation, or Edible Crop Slow-rate Land Application Systems | 75 |
| Domestic Wastewater Residuals 62-640.700(4)(b) | Domestic Wastewater Residuals Land Application Areas | 500 |
| Phosphogypsum Management 62-673.340(2)(d) | Phosphogypsum Stack Systems | 500 (c) |
| Storage Tank Systems 62-761.500(1)(a) and 62-762.501(1)(a) | Aboveground or Underground Storage Tanks | 100 |
| Solid Waste Management Facilities 62-701.300(2)(b) | Solid Waste Disposal Facilities | 500 |
| 62-701.300(12)(a) | Yard Trash Disposal, Storage, or Processing (no setback required for on-site water wells) | 100 |
| 62-701.300(13) | Storage or Treatment of Solid Waste in Tanks | 100 |
| Drinking Water Systems 64E-8.002(2) | Onsite Sewage Treatment and Disposal Systems | 200 (d), 100 (e) |
|  | Sanitary Hazard | 100 (f), (g) |
| Feedlot and Dairy Wastewater Treatment and Management Requirements 62-670.500(6)(a) | Dairy Farm Waste – Unlined Storage and Treatment, or High Intensity Areas | 300 |
| 62-670.500(6)(b) | Dairy Farm Waste – Land Application | 200 |

| Part C Private Wells Multifamily Wells |  |  |  |  |
| --- | --- | --- | --- | --- |
| RULE | INSTALLATION |  | SETBACK in feet (footnote) |  |
| Reuse of Reclaimed Water and Land Application 62-610.421(3) | Slow Rate Land Application Restricted Public Access |  | 500 (a) |  |
| 62-610.521(2) | Rapid Rate Land Application |  | 500 (b) |  |
| 62-610.621(2) | Overland Flow Systems |  | 100 |  |
| 62-610.471(1) | Public Access, Residential Irrigation, or Edible Crop Slow-rate Land Application Systems |  | 75 |  |
| Domestic Wastewater Residuals 62-640.700(4)(b) | Domestic Wastewater Residuals Land Application Areas |  | 300 |  |
| Storage Tank Systems 62-761.500(1)(a) and 62-762.501(1)(a) | Aboveground or Underground Storage Tanks |  | 100 |  |
| Solid Waste Management Facilities 62-701.300(2)(b) | Solid Waste Disposal Facilities |  | 500 |  |
| 62-701.300(12)(a) | Yard Trash Disposal, Storage, or Processing (no set back required for on-site water wells) |  | 100 |  |
| 62-701.300(13) | Storage of Treatment of Solid Waste in Tanks |  | 100 |  |
| Drinking Water Systems 64E-8.003(1) | Onsite Sewage Treatment and Disposal Systems |  | 75 |  |
|  | Sanitary Hazard |  | 75 (f), (g) |  |
| Feedlot and Dairy Wastewater Treatment and Management Requirements 62-670.500(6)(a) | Dairy Farm Waste – Unlined Storage and Treatment, or High Intensity Areas |  | 300 |  |
| 62-670.500(6)(b) | Dairy Farm Waste – Land Application |  | 200 |  |

| Part D Irrigation Wells and Geothermal Wells |  |  |
| --- | --- | --- |
| RULE | INSTALLATION | SETBACK in feet (footnote) |
| Standards for Onsite Sewage Treatment and Disposal Systems 64E-6.005(1)(d) | Onsite Sewage Treatment and Disposal System | 50 |

TABLE I FOOTNOTES

(a) This distance shall be reduced to 200 feet if facility Class I reliability is provided and shall be reduced to 100 feet if both facility Class I reliability and high-level disinfection are provided.

(b) This distance shall be reduced to 200 feet if both facility Class I reliability and high-level disinfection are provided and if the applicant provides reasonable assurance that applicable water quality standards will not be violated at the point of withdrawal.

(c) This distance applies only to shallow water supply wells (i.e., potable water wells that pump from an unconfined water table aquifer).

(d) This distance applies to public drinking water supply wells that serve water systems having total sewage flows greater than 2,000 gallons per day.

(e) This distance applies to public drinking water supply wells that serve water systems having total sewage flows less than or equal to 2,000 gallons per day.

(f) This distance applies to sanitary hazards that pose a potentially high risk to ground water quality and public health as defined in subsection 62-555.312(3), F.A.C. The following examples are of sanitary hazards that pose a potentially high risk: active or abandoned mines; airplane or train fueling or maintenance areas at airports and railroad yards; concentrated aquatic animal production facilities; domestic wastewater collection/transmission systems; drainage or injection wells, oil or gas production wells, and improperly constructed or abandoned wells (i.e., wells not constructed or abandoned in accordance with Chapter 62-532, F.A.C.); fertilizer, herbicide, or pesticide storage areas at agricultural sites, golf courses, nurseries, and parks; graveyards; impoundments and tanks that process, store, or treat domestic wastewater, domestic wastewater residuals, or industrial fluids or waste and that are not regulated under Rule 62-670.500, F.A.C.; industrial waste land application areas other than those regulated under Rule 62-670.500, F.A.C.; junkyards and salvage or scrap yards; pastures with more than five grazing animals per acre; cattle dip vats; pipelines conveying petroleum products, chemicals, or industrial fluids or wastes; and underground storage tanks that are not regulated under Chapter 62-761, F.A.C., but are used for bulk storage of a liquid pollutant or hazardous substance (as defined in Chapter 62-761, F.A.C.) other than sodium hypochlorite solution.

(g) This distance applies to sanitary hazards that pose a potentially moderate risk to ground water quality and public health as defined in subsection 62-555.312(3), F.A.C. The following examples are of sanitary hazards that pose a moderate risk: aboveground storage tanks that are not regulated under Chapter 62-762, F.A.C., but are used for bulk storage of a liquid pollutant or hazardous substance (as defined in Chapter 62-762, F.A.C.) other than sodium hypochlorite solution; fertilizer, herbicide, or pesticide application areas that are not under the ownership or control of the supplier of water at agricultural sites, golf courses, nurseries, and parks; railroad tracks; stormwater detention or retention basins; and surface water (the surface water setback does not apply to multi-family and private wells).

Rulemaking Authority 373.309 FS. Law Implemented 373.309, 373.313, 373.316 FS. History–New 10-7-10.